## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0125-39
Ngaøy/ Date: |  | 2013-01-25 |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse, 3copies | [9 empty] | Trang 1/3
1 | Khaùch haøng/ Custommer |  |  |  |  | : | COÂNG TY TNHH MOÄT THAØNH VIEÂN CÔ KHÍ KIEÂN GIANG (KIMEC).
2. | Đòa chæ/ Address |  |  |  |  | : | 181-Caùch Maïng Thaùng Taùm-P.Vónh Lôïi-TP.Raïch Giaù-tænh Kieân Giang.
3. | Coâng trình/ Project |  |  |  |  | : | SPC-KFW-14W-KG-CKKG.
Goùi thaàu: SPC-KFW-14W-KG.Xaây laép ñöôøng daây vaø traïm Huyeän
An Minh tænh Kieân Giang.
Döï AÙn: Naâng cao hieäu quaû naêng löôïng khu vöïc noâng thoân
4. | Teân Maãu |  |  |  |  | : | TRUÏ ÑIEÄN BEÂ TOÂNG LY TAÂM DÖÏ ÖÙNG LÖÏC 7.5m-F300 .
| Name of sample | [5 empty] | Prestressed centrifugal concrete electrical pole
5. | Kyù hieäu maãu |  |  |  |  | : | 7.5m-F300-SOÁ 427-05/01
Code of sample
6. | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 truï/ pole
7. | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847 : 1994; TCXD 162 : 2004
Test method
8. | Yeâu caàu thöû nghieäm |  |  |  |  | : | Kích thöôùc cô baûn,Maùc Beâ toâng,Löïc ñaàu truï.
Test requirement
9. | Ngaøy thí nghieäm |  |  |  |  | : | 23/01/2013.
Testing date
10. | Keát quaû/ Test result |  |  |  |  | :
Döïa theo tieâu chuaån 5847:1994 vaø baûn veõ thieát keá coät ñieän 7.5m cuûa COÂNG TY TNHH MTV
CÔ KHÍ KIEÂN GIANG, keát quaû thöû nghieäm coät ñieän cho thaáy :
Based on TCVN 5847 : 1994 and designed drawing for Electrical pole type 7.5m of result of
COÂNG TY TNHH MTV CÔ KHÍ KIEÂN GIANG, the tested result of the testd pole show that:
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
Dimension
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
Grade of concrete
| - Thöû löïc keùo ñaàu coät | [7 empty] | : | Ñaït yeâu caàu/ Pass
Tensile load at the top of pole test
Ngöôøi thöïc hieän | [6 empty] | P.Phoøng TN | [5 empty] | P.Giaùm Ñoác
Test By | [6 empty] | Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyeãn Ngoïc Giang | [5 empty] | Nguyeãn Vaên Hoàng Chi
1. Caùc keát quûa thöû nghieäm ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0125-39
Ngaøy/ Date: |  | 2013-01-25 |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse, 3copies | [9 empty] | Trang 2/3
Sketch for tensile load test at the the top of pole
11. | Ñieàu kieän thöû nghieäm
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
Tape rule 20 m, measuring range 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) Mpa, type N
- Löïc keá coù thang ño 1000 kgf, vaïch chia 01 kgf.
Dynamometer measuring range 1000 kgf, division 01 kgf.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,02 mm.
Graduated microscope, measuring range 4 mm, division of 0,02 mm.
| - Cöôøng ñoä neùn beâ toâng coät theo thieát keá : | [8 empty] | 40 | MPa
| Concrete with design grade : | [6 empty] | 40 | MPa
| - Thöû keùo ñaàu coät danh ñònh : | [6 empty] | 300 | kgf
| Nominal load test at the top of pole : | [7 empty] | 300 | kgf
Coät ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá : CKKG TA 7.5-30 - 01/2011 cuûa
COÂNG TY TNHH MTV CÔ KHÍ KIEÂN GIANG
Electrical pole was produced base on the designed drawing ref :CKKG TA 7.5-30 - 01/2011
of COÂNG TY TNHH MTV CÔ KHÍ KIEÂN GIANG.
1. Caùc keát quûa thöû nghieäm ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0125-39
Ngaøy/ Date: |  | 2013-01-25 |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse, 3copies | [9 empty] | Trang 3/3
12. | Keát quaû thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  |  | Ñaùnh giaù Comments
1 | 7.5m-F300-SOÁ 427-05/01 |  |  | 1. Kích thöôùc/ Dimension | [6 empty] | mm
|  |  |  | - | Chieàu daøi/ Length | [6 empty] | 7500± 25 |  | 7510 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 160 ± 5 |  | 160
Outside diameter at top
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 50+7-5 |  | 53
Wall-thickness at top
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 240 ± 5 |  | 240
Outside diameter at bottom
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 60+7-5 |  | 62
Wall-thickness at bottom
|  |  |  | 2. Cöôøng ñoä neùn beâ toâng (baèng buùa thöû) | [6 empty] | MPa | 40 |  | 47 |  |  | Ñaït/ Pass
Compressive strength of concrete
(concrete Hammer Test)
|  |  |  | 3. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,30 |  | 0.15 |  |  | Ñaït/ Pass
Width of the maximum crack at Pn
|  |  |  | 4. Löïc keùo ñaàu coät/ Tensile load at the top pole | [7 empty] | 25% | 50% | 75% |  | 100% | Xaû taûi
[11 empty] | kgf | 75 | 150 | 225 |  | 300 | Deload
|  |  |  | - | Ñoä dòch chuyeån/ Deformation | [5 empty] | mm
|  |  |  | ÔÛ vò trí 1/ at position 1 | [7 empty] | 18 | 37 | 110 |  | 205 | 13
|  |  |  | ÔÛ vò trí 2/ at position 2 | [7 empty] | 13 | 26 | 85 |  | 120 | 8
|  |  |  | ÔÛ vò trí 3/ at position 3 | [7 empty] | 6 | 14 | 52 |  | 81 | 7
|  |  |  | ÔÛ vò trí 4/ at position 4 | [7 empty] | 2 | 6 | 26 |  | 34 | 3
|  |  |  | ÔÛ vò trí 5/ at position 5 | [7 empty] | 1 | 3 | 5 |  | 8 | 1
|  |  |  | - | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 4 |  | 18 | 0
Quantity of visual cracks
|  |  |  | - | Beà roäng cuûa veát nöùt lôùn nhaát, | [5 empty] | mm | 0 | 0 | 0.05 |  | 0.15 | 0
Width of the maximum cracks
|  |  |  | - | Löïc keùo phaù huûy/ Breaking load | [5 empty] | kgf
1. Caùc keát quûa thöû nghieäm ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
L=
L= 7500
00
1000
00
1500
00
1500
00
1500
00
1500
00
1000
00