## COT TRON
1 | 2 |  | 3 | 4 | [9 empty] | 5 | 6 |  | 7 | 8 | 9 | 10
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [16 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [16 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [16 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [16 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [10 empty] | LAS-XD 506
0317-97
Ngaøy/ Date: |  | 25/08/2011 |  |  | Ban haønh laàn 1, soá baûn 05/ The 1st isuse, 5copies | [10 empty] | Trang 1/3
1. | Khaùch haøng/ Custommer |  |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM AN GIANG
2. | Đòa chæ/ Address |  |  |  |  | : | Quoác loä 91, phöôøng Myõ Thôùi, TP.Long Xuyeân, tænh An Giang
3. | Coâng trình/ Project |  |  |  |  | : | Goùi thaàu soá 16W Xaây laép ñöôøng daây vaø traïm
bao goàm 8 Xaõ : Löu Nghieäp Anh, Thanh Sôn, Kim Sôn, Ñoân Chaâu,
Haøm Giang, Ñoân Xuaân, Ñaïi An, Ñònh An, thuoäc H.Traø Cuù, tænh Traø Vinh
4. | Teân Maãu |  |  |  |  | : | COÄT ÑIEÄN BEÂ TOÂNG LY TAÂM ÖÙNG LÖÏC TRÖÔÙC 7,5B-PC-300 (tieáp ñòa)
| Name of sample | [5 empty] | Prestressed centrifugal concrete electrical pole
5. | Kyù hieäu maãu |  |  |  |  | : | 7,5B-PC-300, soá 450- 06/2011
Code of sample
6. | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 truï/ pole
7. | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Reference TCVN 5847 : 1994; TCXD 162 : 2004
Test method
8. | Yeâu caàu thöû nghieäm |  |  |  |  | : | Theo yeâu caàu cuûa khaùch haøng/ Requirement s custommer
Test requirement
9. | Ngaøy thí nghieäm |  |  |  |  | : | 23/08/2011
Testing date
10. | Keát quaû/ Test result |  |  |  |  | :
Döïa theo tieâu chuaån 5847 : 1994 vaø baûn veõ thieát keá coät ñieän 7,5m cuûa COÂNG TY COÅ PHAÀN
BEÂ TOÂNG LY TAÂM AN GIANG, keát quaû thöû nghieäm coät ñieän cho thaáy :
Based on TCVN 5847 : 1994 and designed drawing for Electrical pole type 7,5 m of result of
AN GIANG CENTRIFUGED CONCRTE JOINT STOCK COMPANY, the tested result of the
tested pole show that :
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
Dimension
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
Grade of concrete
| - Thöû löïc keùo ñaàu coät | [7 empty] | : | Ñaït yeâu caàu/ Pass
Tensile load at the top of pole test
Ngöôøi thöïc hieän | [6 empty] | TP Phoøng TN | [5 empty] | Giaùm Ñoác
Test By | [6 empty] | Chef of Laboratory | [5 empty] | Director
Nguyeãn Huy Tieán | [6 empty] | Nguyeãn Vaên Hoàng Chi | [5 empty] | Nguyeãn Ñaêng Khoa
1. Caùc keát quûa thöû nghieäm ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [19 empty] | 07.07WP09.R0-From07.07-REP38.R0
PKQ:0317-97 |  |  |  |  | KẾT QUAÛ THỬ NGHIỆM TIEÁP THEO/CONTINUE | [11 empty] | LAS-XD 506
Trang 2/3
Sketch for tensile load test at the the top of pole
11. | Ñieàu kieän thöû nghieäm
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
- Thöôùc theùp daøi 10 m, vaïch chia 1 mm
Tape rule 10 m, measuring range 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) MPa, type N
- Löïc keá coù thang ño 1000 kgf, vaïch chia 01 kgf.
Dynamometer measuring range 1000 kgf, division 01 kgf.
- Kính phoùng ñaïi 5 mm, vaïch chia 0,05 mm.
Graduated microscope, measuring range 5 mm, division of 0,05 mm.
| - Cöôøng ñoä neùn beâ toâng coät theo thieát keá : | [8 empty] | 40 MPa
| Concrete with design grade : | [6 empty] | 40 MPa
| - Thöû keùo ñaàu coät danh ñònh : | [6 empty] | 300 kgf
| Nominal load test at the top of pole : | [7 empty] | 300 kgf
- Coät ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá : 01/7,5B-PC-300/ACECO/02-07 cuûa COÂNG TY
COÅ PHAÀN BEÂ TOÂNG LY TAÂM AN GIANG
Electrical pole was produced base on the designed drawing ref 01/7,5B-PC-300/ACECO/02-07
AN GIANG CENTRIFUGED CONCRTE JOINT STOCK COMPANY
1. Caùc keát quûa thöû nghieäm ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [19 empty] | 07.07WP09.R0-From07.07-REP38.R0
PKQ:0317-97 |  |  |  |  | KẾT QUAÛ THỬ NGHIỆM TIEÁP THEO/CONTINUE | [11 empty] | LAS-XD 506
Trang 3/3
12. | Keát quaû thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  |  | Keát quaû thöû nghieäm Test result |  |  |  | Ñaùnh giaù Comments
1 | 7,5B-PC-300, soá 450- 06/2011 |  |  | 1. Kích thöôùc/ Dimension | [6 empty] | mm
|  |  |  | - | Chieàu daøi/ Length | [6 empty] | 7500 |  |  | 7500 |  |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 160 |  |  | 161
Outside diameter at top
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 50 |  |  | 52
Wall-thickness at top
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 240 |  |  | 242
Outside diameter at bottom
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 60 |  |  | 61
Wall-thickness at bottom
|  |  |  | 2. Cöôøng ñoä neùn beâ toâng (baèng buùa thöû) | [6 empty] | MPa | 40 |  |  | 48,0 |  |  |  | Ñaït/ Pass
Compressive strength of concrete
(concrete Hammer Test)
|  |  |  | 3. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,30 |  |  | 0,1 |  |  |  | Ñaït/ Pass
Width of the maximum crack at Pn
|  |  |  | 4. Löïc keùo ñaàu coät/ Tensile load at the top pole | [6 empty] | kN(kgf) | 25% (75) | 50% (150) |  | 75% (225) |  | 100% (300) |  | Xaû taûi Deload
|  |  |  | - | Ñoä dòch chuyeån/ Deformation | [5 empty] | mm
|  |  |  | ÔÛ vò trí 1/ at position 1 | [7 empty] | 38 | 68 |  | 124 |  | 252 |  | 8
|  |  |  | ÔÛ vò trí 2/ at position 2 | [7 empty] | 26 | 48 |  | 86 |  | 182 |  | 6
|  |  |  | ÔÛ vò trí 3/ at position 3 | [7 empty] | 14 | 28 |  | 50 |  | 108 |  | 4
|  |  |  | ÔÛ vò trí 4/ at position 4 | [7 empty] | 6 | 14 |  | 22 |  | 48 |  | 2
|  |  |  | ÔÛ vò trí 5/ at position 5 | [7 empty] | 0 | 0 |  | 2 |  | 2 |  | 0
|  |  |  | - | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 |  | 0 |  | 12 |  | 0
[5 empty] | Quantity of visual cracks | [5 empty] | no
|  |  |  | - | Beà roäng cuûa veát nöùt lôùn nhaát, | [5 empty] | mm | 0 | 0 |  | 0 |  | 0,1 |  | 0
Width of the maximum cracks
|  |  |  | - | Löïc keùo phaù huûy/ Breaking load | [5 empty] | kN(kgf)
1. Caùc keát quûa thöû nghieäm ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [19 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
L=
L= 7500
00
1000
00
1500
00
1500
00
1500
00
1500
00
300
00