## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0914-01
Ngaøy/Date: |  | 14/9/2018. |  |  | Ban haønh laàn 1, soá baûn 03 / The 1st isuse, 03 copies | [9 empty] | Trang 1/3
1 | Teân Maãu/Sample name |  |  |  |  | : | TRUÏ ÑIEÄN BTLT TIEÀN AÙP-Loaïi 7.5 m- 200 kGf-TIEÁP ÑÒA-N=2.
2 | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 truï / pole
3 | Ngaøy thöû/Testing date |  |  |  |  | : | 11/9/2018.
4 | Chuû Ñaàu Tö/Proj.Investor |  |  |  |  | : | COÂÂNG TY ÑIEÄN LÖÏC TAÂY NINH.
5 | Nhaø Thaàu/Contractor |  |  |  |  | : | COÂNG TY COÅ PHAÀN XAÂY DÖÏNG THAÊNG LONG.
6 | Ñôn vò yeâu caàu/Custommer |  |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM THUÛ ÑÖÙC 1(TDC1 JSC).
7 | Ñòa chæ / Address |  |  |  |  | : | SOÁ 234-ÑT 747-AÁP THANH LÖÔNG-X THAÏNH PHÖÔÙC-H.TAÂN UYEÂN-T. BÌNH DÖÔNG.
8 | Coâng trình/ Project |  |  |  |  | : | XAÂY LAÉP 02 COÂNG TRÌNH:"XAÂY DÖÏNG MÔÙI Ä ÑÖÔØNG DAÂY TRUNG AÙP VAØ TRAÏM BIEÁN AÙP HUYEÄN TRAÛNG BAØNG","XAÂY DÖÏNG MÔÙI ÑÖÔØNG DAÂY TRUNG AÙP VAØ 6 TBA 250 KVA;1 TBA 3X50 KVA;18 TBA 50 KVA HUYEÄN GOØ DAÀU".
9 | Ñòa ñieåm / Project Add. |  |  |  |  | : | TÆNH TAÂY NINH.
10 | Kyù hieäu maãu/ |  |  |  |  | : | 7.5m-200-TÑ-N=2- Soá 20 -NSX 31/8/2018.
Code of sample
11 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847: 2016; TCVN 9334 : 2012.
Test method
12 | Ñieàu kieän thöû nghieäm
Maãu ñöôïc thöû nghieäm taïi nhaø maùy : soá 234- ÑT 747,AÁp Taân Löông,Xaõ Thaïnh Phöôùc,Huyeän Taân Uyeân- Tænh Bình Döông, coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan. The sample was tested at Factory - of TDC1 Company , with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá : | [6 empty] | 40 | MPa
Concrete with design grade :
| - Thöû keùo ñaàu truï danh ñònh Pn : | [7 empty] | 2 | KN | 204 | KGF
Nominal load test at the top of pole :
| - Thöû keùo ñaàu truï Phaù huûy N=2 ; Pu | [7 empty] | 4 | KN | 408 | KGF
Breaking Load test at the top of pole : Pu max
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: 7.5-200-N=2-TDC1/01 ,thaùng 05/2014 cuûa COÂNG TY COÅ PHAÀN BTLT THUÛ ÑÖÙC 1 (TDC1). Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing No: 7.5-200-N=2-TDC1/01; 05/2014 of THUDUC 1 JSC(TDC1).
Ngöôøi thöïc hieän | [6 empty] | Tröôûng Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyeãn Vaên Hoàng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0914-01
Ngaøy/Date: |  | 14/9/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây:
The test was carried out as the sketch below
Sketch for tensile load test at the the top of pole
13 | Thieát bò thöû nghieäm chính:
Main equipment fo testing
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
Tape rule 20 m, measuring range 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) MPa, type N
- Löïc keá coù thang ño 2000 kgf, vaïch chia 1 kgf.
Dynamometer measuring range 2000 kgf, division 1 kgf.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
Graduated microscope, measuring range 4mm, division of 0,05mm.
- Boä caên laù 0.02 ñeán 1.00 mm.
Feeler gauge range 0.02 to 1.00 mm.
14 | Keát quaû thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  |  | Ñaùnh giaù Comments
1 | 7.5m-200-TÑ-N=2- Soá 20 -NSX 31/8/2018. |  |  | 1. Kích thöôùc/ Dimension | [6 empty] | mm
|  |  |  | - | Chieàu daøi/ Length | [6 empty] | 7500(+25;-10) |  | 7500 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 160 (+4;-2) |  | 162
Outside diameter at top
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 50 (+7;-5) |  | 49
Wall-thickness at top
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 250 (+4;-2) |  | 251
Outside diameter at bottom
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 60 (+7;-5) |  | 60
Wall-thickness at bottom
|  |  |  | 2. Cöôøng ñoä neùn beâ toâng (baèng buùa thöû) | [6 empty] | MPa | min 40 |  | 56 |  |  | Ñaït/ Pass
Compressive strength of concrete
(concrete Hammer Test)
|  |  |  | 3. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,25 |  | 0 |  |  | Ñaït/ Pass
Width of the maximum crack at Pn
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0914-01
Ngaøy/Date: |  | 14/9/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | 7.5m-200-TÑ-N=2- Soá 20 -NSX 31/8/2018. |  |  | 4. Löïc keùo ñaàu truï/ Tensile load at the top pole | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
[12 empty] | 0.5 | 1 | 1.5 |  | 2 | Deload
|  |  |  | - | Ñoä dòch chuyeån/ Deformation | [5 empty] | mm
|  |  |  | ÔÛ vò trí 1/ at position 1 | [7 empty] | 16 | 27 | 38 |  | 62 | 8
|  |  |  | ÔÛ vò trí 2/ at position 2 | [7 empty] | 8 | 16 | 25 |  | 36 | 5
|  |  |  | ÔÛ vò trí 3/ at position 3 | [7 empty] | 4 | 8 | 13 |  | 21 | 3
|  |  |  | ÔÛ vò trí 4/ at position 4 | [7 empty] | 2 | 5 | 7 |  | 9 | 2
|  |  |  | ÔÛ vò trí 5/ at position 5 | [7 empty] | 1 | 2 | 3 |  | 4 | 1
|  |  |  | - | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks
|  |  |  | .- | Soá löôïng veát nöùt noái tieáp voøng quanh thaân truï | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks,continuous on the pole.
|  |  |  | - | Beà roäng cuûa veát nöùt lôùn nhaát, | [5 empty] | mm | 0 | 0 | 0 |  | 0 | 0
Width of the maximum cracks
|  |  |  | - | Löïc keùo tôùi haïn Pu; N=2.0 | [5 empty] | (kGf) | TRUÏ CHÖA PHAÙ HUÛY KHI Pu=K2=4.0 KN (410 KGF)
Breaking Load Pmax
15 | Nhaän xeùt/ Comments |  |  |  |  | :
Caên cöù tieâu chuaån 5847 : 2016 vaø baûn veõ thieát keá truï ñieän 7.5-200-N=2-TDC1/01; 05/2014 cuûa COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM THUÛ ÑÖÙC 1.Keát quaû thöû nghieäm cho thaáy :
Based on TCVN 5847: 2016 and designed drawing for PCRC Electricad pole type 7.5-200-N=2-TDC1/01; 05/2014 result of THUDUC1 JSC CO.,the above test result of the tested pole show that:
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
Dimension
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
Grade of concrete
| - Thöû löïc keùo ñaàu truï | [7 empty] | : | Ñaït yeâu caàu/ Pass
Tensile load at the top of pole test
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
L=7500
1300
1500
1500
1500
1500
250