## CAU KIEN BT
1 | 2 |  | 3 | 4 | [5 empty] | 5 | 6 |  | 7 | 8 | 9 | 10
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [12 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [12 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [12 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [12 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [6 empty] | LAS-XD 506
0914-03
Ngaøy/Date: |  | 14/09/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse, 3 copies | [6 empty] | Trang 1/1
1 | Teân Maãu/Sample name |  |  |  |  | : | ÑAØ CAÛN BTCT 1200x200/ POLE FOUNDATION 1200x200.
2 | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 / element.
3 | Ngaøy thöû/Testing date |  |  |  |  | : | 11/09/2018.
4 | Chuû Ñaàu Tö/Proj.Investor |  |  |  |  | : | COÂNG TY ÑIEÄN LÖÏC TAÂY NINH.
5 | Nhaø Thaàu/Contractor |  |  |  |  | : | COÂNG TY COÅ PHAÀN XAÂY DÖÏNG THAÊNG LONG.
6 | Ñôn vò yeâu caàu/Custommer |  |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM THUÛ ÑÖÙC 1.
7 | Ñòa chæ / Address |  |  |  |  | : | SOÁ 234-ÑT 747-AÁP THANH LÖÔNG-X THAÏNH PHÖÔÙC-H.TAÂN UYEÂN-T. BÌNH DÖÔNG.
8 | Coâng trình/ Project |  |  |  |  | : | XAÂY LAÉP 02 COÂNG TRÌNH:"XAÂY DÖÏNG MÔÙI Ä ÑÖÔØNG DAÂY TRUNG AÙP VAØ TRAÏM BIEÁN AÙP HUYEÄN TRAÛNG BAØNG","XAÂY DÖÏNG MÔÙI ÑÖÔØNG DAÂY TRUNG AÙP VAØ 6 TBA 250 KVA;1 TBA 3X50 KVA;18 TBA 50 KVA HUYEÄN GOØ DAÀU".
9 | Ñòa ñieåm / Project Add. |  |  |  |  | : | TÆNH TAÂY NINH.
10 | Kyù hieäu maãu/ |  |  | Code of sample |  |  | ÑC1200X200 - MS 14 -T 08/2018.
11 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847:1994; TCVN 9334:2012;TCXDVN 239:2006.
Test method
12 | Ñieàu kieän thöû nghieäm / Test condition:
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) Mpa, type N
- Ñaø caûn ñöôïc saûn xuaát theo baûn veõ: EVN 0202, T 10/2014 cuûa Coâng Ty Tö Vaán Ñieän Mieàn Nam-Toång Coâng Ty Ñieän Löïc Mieàn Nam.
Pole foundation were produced base on the designed drawing No: EVN 0202/T 10/2014 of SOUTHERN CONSULTANT ELECTRICITY COMPANY - SPC-EVN.
- Treân moãi caáu kieän ñöôïc thöû nghieäm taïi 3 vuøng khaùc nhau, moãi vuøng thöû nghieäm coù dieän tích
khoaûng (200 x 300) mm, ñöôïc maøi nhaün vaø thöû 10 ñieåm baèng buùa thöû.
On the each testing element was tesedt in 3 positions.In each test position about (200X300) mm,which was ground smooth,
took 10 rebound readings.
13 | Keát quaû/ Test result :
| Teân caáu kieän |  |  | Tình traïng beà maët beâ toâng |  |  |  | Cöôøng ñoä neùn öôùc tính.MPa ( baèng buùa thöû) |  | Kích thöôùc/Dimension, mm
| Name of element |  |  | Concrete surface status |  |  |  | Estimated Compressive strength , MPa |  | Daøi / Length |  |  | Roäng/ Broard |  | Cao / High
| ÑC1200X200 - MS 14 -T 08/2018. |  |  | Khoâ,Khoâng nöùt, Roã |  |  |  | 26 (min20) |  | 1203 |  |  | 205 |  | 201/64
| NHAÄN XEÙT |  |  | ÑAÏT YEÂU CAÀU |  |  |  | ÑAÏT YEÂU CAÀU |  | ÑAÏT YEÂU CAÀU
Ngöôøi thöïc hieän | [6 empty] | Phoøng TN |  | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory |  | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyễn Văn Hồng Chi |  | Nguyeãn Thò Thuûy
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [8 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only | [8 empty] | 07.07WP09.R0-From07.07-REP38.R0