## CAU KIEN BT
1 | 2 |  | 3 | 4 | [5 empty] | 5 | 6 |  | 7 | 8 | 9 | 10
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [12 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [12 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [12 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [12 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [6 empty] | LAS-XD 506
1024-03
Ngaøy/Date: |  | 24/10/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse, 3 copies | [6 empty] | Trang 1/1
1. | Khaùch haøng/ Custommer |  |  |  |  | : | COÂNG TY TNHH SAÛN XUAÁT TRUÏ ÑIEÄN VAØ CÔ KHÍ TIEÀN PHONG.
COÂNG TY ÑIEÄN LÖÏC TAÂY NINH.
2. | Ñòa chæ/ Address |  |  |  |  | : | 36-ÑIEÄN BIEÂN PHUÛ-P.15-Q.BÌNH THAÏNH-TP. HOÀ CHÍ MINH.
3. | Coâng trình/ Project |  |  |  |  | : | XAÂY DÖÏNG LOÄ RA MBA 2T TRAÏM 110/22kV SUOÁI ÑOÄP-THUOÄC DÖÏ AÙN :ÑAÀU TÖ XAÂY DÖÏNG CAÙC COÂNG TRÌNH LÖÔÙI ÑIEÄN NAÊM 2018.
4. | Teân Maãu/Name of sample |  |  |  |  | : | ÑAØ CAÛN BTCT 1.2m/ POLE FOUNDATION 1.2m.
5. | Kyù hieäu maãu |  |  |  |  | : | ÑC 1,2m- SOÁ : 06 -T10/2018.
Code of sample
6. | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 caáu kieän/ element
7. | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 9334:2012; TCVN 5847:1994.
Test method
8 | Ngaøy thí nghieäm |  |  |  |  | : | 22/10/2018.
Testing date
9 | Ñieàu kieän thöû nghieäm / Test condition:
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) Mpa, type N
- Ñaø caûn ñöôïc saûn xuaát theo baûn veõ : SOÁ 9056-XD-TATP-ÑC1.2 ; do Coâng Ty Tö Vaán Xaây Döïng Ñieän 3( PECC3-EVN ) Thieát Keá.
Pole foundation were produced base on the designed drawing No : 9056-XD-TATP-ÑC 1.2 ; of POWER ELECTRICITY CONSULTANT CONSTRUCTION COMPANY 3 (PECC3 EVN ).
- Treân moãi caáu kieän ñöôïc thöû nghieäm taïi 3 vuøng khaùc nhau, moãi vuøng thöû nghieäm coù dieän tích
khoaûng (200 x 300) mm, ñöôïc maøi nhaün thöû 10 ñieåm baèng buùa thöû.
On the each testing element was tested in 3 positions. In each test position about (200X300)mm,wich was ground smooth,
took 10 rebound readings.
10. | Keát quaû/ Test result :
| Teân caáu kieän |  |  | Tình traïng beà maët beâ toâng |  |  |  | Cöôøng ñoä neùn öôùc tính.MPa ( baèng buùa thöû) |  | Kích thöôùc/Dimension, mm
| Name of element |  |  | Concrete surface status |  |  |  | Estimated Compressive strength , MPa |  | Daøi / Length |  |  | Roäng/ Broard |  | Cao / High
| ÑC 1,2m- SOÁ : 06 -T10/2018. |  |  | Khoâ,Khoâng nöùt, Roã |  |  |  | 28 (min20) |  | 1205 |  |  | 203 |  | 205/64
| NHAÄN XEÙT |  |  | ÑAÏT YEÂU CAÀU |  |  |  | ÑAÏT YEÂU CAÀU |  | ÑAÏT YEÂU CAÀU
Ngöôøi thöïc hieän | [6 empty] | Tröôûng Phoøng TN |  | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory |  | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyễn Văn Hồng Chi |  | Nguyeãn Thò Thuûy
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [8 empty] | 07.07WP09.R0-From07.07-REP38.R0
1.Test result are valid for the namely submitted samples only | [8 empty] | 07.07WP09.R0-From07.07-REP38.R0
L=