## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1024-02
Ngaøy/Date: |  | 24/10/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 1/3
1 | Teân Maãu/Sample name |  |  |  |  | : | TRUÏ ÑIEÄN BTLT TIEÀN AÙP-Loaïi 12m-5.4kN (551 kGf),K=2.
2 | Soá löôïng maãu/Quantity |  |  |  |  | : | 01 truï / pole
3 | Ngaøy thöû/Testing date |  |  |  |  | : | 22/10/2018.
4 | Khaùch haøng/Custommer |  |  |  |  | : | COÂNG TY TNHH SAÛN XUAÁT TRUÏ ÑIEÄN VAØ CÔ KHÍ TIEÀN PHONG.
COÂNG TY ÑIEÄN LÖÏC TAÂY NINH.
5 | Ñòa chæ / Address |  |  |  |  | : | 36 ÑIEÄN BIEÂN PHUÛ-PHÖÔØNG 15-QUAÄN BÌNH THAÏNH-TP.HOÀ CHÍ MINH.
6 | Coâng trình/ Project |  |  |  |  | : | XAÂY DÖÏNG LOÄ RA MBA 2T TRAÏM 110/22kV SUOÁI ÑOÄP-THUOÄC DÖÏ AÙN :ÑAÀU TÖ XAÂY DÖÏNG CAÙC COÂNG TRÌNH LÖÔÙI ÑIEÄN NAÊM 2018.
7 | Kyù hieäu maãu/ |  |  |  |  | : | PC.I-12m-190-5.4 kN,K=2 -Soá : 5391.
Code of sample
8 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847:2016; TCVN 9334:2012.
Test method
9 | Ñieàu kieän thöû nghieäm
Maãu ñöôïc thöû nghieäm taïi Xöôûng saûn xuaát Soá 02 :C14/24,QL 1A,AÁp 3,Xaõ Taân Kieân,Huyeän Bình Chaùnh- Tp HCM, coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan. The sample was tested at Workshop -Tien Phong Company Ltd., No 02:C14/24,QL1A,Hamlet No 3,Tan Kien Ward, Binh Chanh District, Ho Chi Minh City , with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá : | [6 empty] | 50 | MPa
Concrete with design grade :
| - Thöû keùo ñaàu truï danh ñònh Pn: kN | [8 empty] | 5.4 | 550.8 | (kGf)
Nominal load test at the top of pole :
| - Thöû keùo ñaàu truï Phaù huûy K=2.0: | [7 empty] | kN | 10.8 | 1101.6 | ( kGf)
Breaking Load test at the top of pole : Pu
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: KC-12-540- K2 ,thaùng 6/2017 cuûa COÂNG TY TNHH TÖ VAÁN THIEÁT KEÁ KIEÅM ÑÒNH XAÂY DÖÏNG NAD. Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing No: KC-12-540-K2; 6/2017 of COÂNG TY TNHH TÖ VAÁN THIEÁT KEÁ KIEÅM ÑÒNH XAÂY DÖÏNG NAD.
Ngöôøi thöïc hieän | [6 empty] | Tröôûng Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyễn Văn Hồng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc keát KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1024-02
Ngaøy/Date: |  | 24/10/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây:
The test was carried out as the sketch below
Sketch for tensile load test at the the top of pole
10 | Thieát bò thöû nghieäm chính:
Main equipment fo testing
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
Tape rule 20 m, measuring range 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) MPa, type N
- Löïc keá coù thang ño 2000 kgf, vaïch chia 01 kgf.
Dynamometer measuring range 2000 kgf, division 01 kgf.
- Boä caên laù töø 0.02 ñeán 1.00 mm.
Feeler gauge range 0.02mm to 1.00 mm.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
Graduated microscope, measuring range 4mm, division of 0,05mm.
11 | Keát quaû thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  |  | Ñaùnh giaù Comments
1 | PC.I-12m-190-5.4 kN,K=2 -Soá : 5391. |  |  | 1. Kích thöôùc/ Dimension | [6 empty] | mm
|  |  |  | - | Chieàu daøi/ Length | [6 empty] | 12000(±25,-10) |  | 12005 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 190 (+4,-2) |  | 192
Outside diameter at top
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 50 (+7;-5) |  | 56
Wall-thickness at top
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 350 (+4,-2) |  | 351
Outside diameter at bottom
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 60 (+7;-5) |  | 62
Wall-thickness at bottom
|  |  |  | 2. Cöôøng ñoä neùn beâ toâng (baèng buùa thöû) | [6 empty] | MPa | min 50 |  | 58 |  |  | Ñaït/ Pass
Compressive strength of concrete
(for Hammer Test)
|  |  |  | 3. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,25 |  | 0.05 |  |  | Ñaït/ Pass
Width of the maximum crack at Pn
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1024-02
Ngaøy/Date: |  | 24/10/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | PC.I-12m-190-5.4 kN,K=2 -Soá : 5391. |  |  | 4. Löïc keùo ñaàu truï / Tensile load at the top pole | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
[12 empty] | 1.35 | 2.7 | 4.05 |  | 5.4 | Deload
[11 empty] | kGf | 137.7 | 275.4 | 413.1 |  | 550.8
|  |  |  | - | Ñoä dòch chuyeån/ Deformation | [5 empty] | mm
|  |  |  | ÔÛ vò trí 1/ at position 1 | [7 empty] | 35 | 75 | 120 |  | 240 | 20
|  |  |  | ÔÛ vò trí 2/ at position 2 | [7 empty] | 20 | 40 | 70 |  | 150 | 10
|  |  |  | ÔÛ vò trí 3/ at position 3 | [7 empty] | 10 | 25 | 40 |  | 80 | 5
|  |  |  | ÔÛ vò trí 4/ at position 4 | [7 empty] | 5 | 10 | 15 |  | 30 | 2
|  |  |  | ÔÛ vò trí 5/ at position 5 | [7 empty] | 0 | 1 | 2 |  | 3 | 1
|  |  |  | - | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 7 | 0
Quantity of the visual cracks
|  |  |  | .- | Soá löôïng veát nöùt noái tieáp voøng quanh thaân truï | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks,continuous on the pole.
|  |  |  | - | Beà roäng cuûa veát nöùt lôùn nhaát, | [5 empty] | mm | 0 | 0 | 0 |  | 0.05 | 0
Width of the maximum cracks
|  |  |  | - | Löïc keùo tôùi haïn Pu (K=2.0) | [5 empty] | kN (kGf) | Pu = 10.8 kN (1102 kGf) ,truï chöa bò phaù huûy.
Breaking Load Pu (max)
12 | Nhaän xeùt/ Comments |  |  |  |  | :
Caên cöù tieâu chuaån 5847:2016 vaø baûn veõ thieát keá truï ñieän 12 m-540-K2;6/2017 cuûa COÂNG TY TNHH TÖ VAÁN THIEÁT KEÁ KIEÅM ÑÒNH XAÂY DÖÏNG NAD.Keát quaû thöû nghieäm truï ñieän cho thaáy :
Based on TCVN 5847:2016 and designed drawing for PCRC Electricad pole type 12m-540-K2; 6/2017 result of COÂNG TY TNHH TÖ VAÁN THIEÁT KEÁ KIEÅM ÑÒNH XAÂY DÖÏNG NAD ,the above test result of the tested pole show that:
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
Dimension
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
Grade of concrete
| - Thöû löïc keùo ñaàu truï | [7 empty] | : | Ñaït yeâu caàu/ Pass
Tensile load at the top of pole test
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
L=12000
2000
2400
2400
2400
2400
250