## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1108-168
Ngaøy/Date: |  | 08/11/2018 |  |  | Ban haønh laàn 1, soá baûn 03 / The 1st isuse, 03 copies | [9 empty] | Trang 1/3
1. | Teân Maãu/ Sample name |  |  |  |  | : | COÄT ÑIEÄN BTLT TIEÀN AÙP-LOAÏI 14-PC-11.0 TÑ, k = 1.5
| Kyù hieäu maãu/ |  |  |  |  | : | 14-PC-11.0, Số 01-10/2018
Code of sample
2. | Coâng trình/ Project |  |  |  |  | : | Boïc hoùa löôùi, naâng cao ñoä tin caäy cung caáp ñieän
huyeän Ba Tri naêm 2018 tuyeán 474, boïc hoùa löôùi
trung theá thaønh phoá Bếân Tre naêm 2018
3. | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 truï / pole
4. | Ngaøy thöû/ Testing date |  |  |  |  | : | 02/11/2018
5. | Ñôn vò yeâu caàu/Custommer |  |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM AN GIANG
| Ñòa chæ/ Address |  |  |  |  | : | Quoác loä 91, phöôøng Myõ Thôùi, TP.Long Xuyeân, tænh An Giang
6. | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847:2016; TCVN 9334:2012.
Test method
7. | Ñieàu kieän thöû nghieäm/ Test condition:
- Maãu ñöôïc thöû nghieäm taïi Coâng ty Coå phaàn Beâ toâng Ly taâm An Giang,
coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan.
The sample was tested at An Giang Centrifuged Concrete Joint Stock Company,
with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá: | [6 empty] | 40 | MPa
Concrete with design grade:
| - Thöû keùo ñaàu coät danh ñònh Pn: | [6 empty] | 11 | kN
Nominal load test at the top of pole:
- Coät ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: 02/14-PC-11.0/ACECO/07-17 cuûa Coâng ty
Coå phaàn Beâ toâng Ly taâm An Giang
Electrical pole was produced based on the designed drawing No. 02/14-PC-11.0/ACECO/07-17
of An Giang Centrifuged Concrete Joint Stock Company
Ngöôøi thöïc hieän | [6 empty] | Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyeãn Vaên Hoàng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1108-168
Ngaøy/Date: |  | 08/11/2018 |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây/ The test was carried out as the sketch below:
Sketch for tensile load test at the the top of pole
8. | Thieát bò thöû nghieäm chính/Main equipment for testing:
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm/ Tape rule 20 m, measuring range 1 mm
- Thöôùc caëp, vaïch chia 0,02 mm/ Vernier caliper, division 0,02 mm
- Boä caên laù 0.02 ñeán 1.00 mm/ Feeler gauge range 0.02 to 1.00 mm
- Kính phoùng ñaïi 4 mm, vaïch chia 0,02 mm
Graduated microscope, measuring range 4 mm, division of 0,05 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N
Concrete test Hammer, measuring range (10-70) MPa, type N
- Löïc keá coù thang ño 3000 kgf, vaïch chia 1 kgf
Dynamometer measuring range 3000 kgf, division 1 kgf
9. | Keát quaû thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  |  | Ñaùnh giaù Comments
1 | 14-PC-11.0, Số 01-10/2018 |  |  | 1. Kích thöôùc/ Dimension | [6 empty] | mm
|  |  |  | - | Chieàu daøi/ Length | [6 empty] | 14000 (+25;-10) |  | 14010 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 190 (+4;-2) |  | 192
Outside diameter at top
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 60 (+7;-5) |  | 62
Wall-thickness at top
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 377 (+4;-2) |  | 378
Outside diameter at bottom
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 80 (+7;-5) |  | 82
Wall-thickness at bottom
|  |  |  | 2. Cöôøng ñoä neùn beâ toâng (baèng buùa thöû) | [6 empty] | MPa | min | 40 | 60 |  |  | Ñaït/ Pass
(Baèng buùa thöû beâ toâng)
Compressive strength of concrete
(concrete Hammer Test)
|  |  |  | 3. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,25 |  | 0.14 |  |  | Ñaït/ Pass
Width of the maximum crack at Pn
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1108-168
Ngaøy/Date: |  | 08/11/2018 |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | 14-PC-11.0, Số 01-10/2018 |  |  | 4. Löïc keùo ñaàu truï | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
|  |  |  | Tensile load at the top pole | [7 empty] | 2.75 | 5.5 | 8.25 |  | 11 | Deload
[11 empty] | (kgf) | 280.3262 | 560.6524 | 840.9786 |  | 1121.3048
|  |  |  | - | Ñoä dòch chuyeån/ Deformation | [5 empty] | mm
|  |  |  | ÔÛ vò trí 1/ at position 1 | [7 empty] | 72 | 168 | 348 |  | 776 | 42
|  |  |  | ÔÛ vò trí 2/ at position 2 | [7 empty] | 44 | 106 | 224 |  | 512 | 29
|  |  |  | ÔÛ vò trí 3/ at position 3 | [7 empty] | 19 | 50 | 113 |  | 260 | 12
|  |  |  | ÔÛ vò trí 4/ at position 4 | [7 empty] | 8 | 17 | 39 |  | 86 | 6
|  |  |  | ÔÛ vò trí 5/ at position 5 | [7 empty] | 0 | 1 | 3 |  | 4 | 0
|  |  |  | - | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 46 | 0
Quantity of the visual cracks
|  |  |  | .- | Soá löôïng veát nöùt noái tieáp voøng quanh thaân coät | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks,continuous on the pole.
|  |  |  | - | Beà roäng cuûa veát nöùt lôùn nhaát, | [5 empty] | mm | 0 | 0 | 0 |  | 0.14 | 0
Width of the maximum cracks
|  |  |  | - | Löïc keùo tôùi haïn Pu: | [5 empty] | kN (kgf)
Breaking Load Pmax
10. | Nhaän xeùt/ Comments:
Caên cöù tieâu chuaån TCVN 5847 : 2016 vaø baûn veõ thieát keá coätï ñieän 14 m cuûa Coâng ty Coå phaàn
Beâ toâng Ly taâm An Giang. Keát quaû thöû nghieäm cho thaáy:
Based on TCVN 5847: 2016 and designed drawing for Electricad pole type 14 m of An Giang
Centrifuged Concrete Joint Stock Company, the above test result of the tested pole show that:
| - Kích thöôùc | [8 empty] | : Ñaït yeâu caàu/ Pass
Dimension
| - Maùc beâ toâng | [8 empty] | : Ñaït yeâu caàu/ Pass
Grade of concrete
| - Thöû löïc keùo ñaàu truï | [8 empty] | : Ñaït yeâu caàu/ Pass
Tensile load at the top of pole test
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
L = 14000
2400
2800
2800
2800
2800
250