## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [10 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [10 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [10 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [10 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [6 empty] | LAS-XD 506
1108-172
Ngaøy/Date: |  | 08/11/2018 |  |  | Ban haønh laàn 1, soá baûn 03 / The 1st isuse, 03 copies | [6 empty] | Trang 1/2
1. | Teân Maãu/ Sample name |  |  |  |  | : | COÄT ÑIEÄN BTLT TIEÀN AÙP-LOAÏI 14-PC-11.0 TÑ, k = 1.5
| Kyù hieäu maãu/ |  |  |  |  | : | 14-PC-11.0, Số 04-10/2018
Code of sample
2. | Coâng trình/ Project |  |  |  |  | : | Boïc hoùa löôùi, naâng cao ñoä tin caäy cung caáp ñieän
huyeän Ba Tri naêm 2018 tuyeán 474, boïc hoùa löôùi
trung theá thaønh phoá Bếân Tre naêm 2018
3. | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 truï / pole
4. | Ngaøy thöû/ Testing date |  |  |  |  | : | 02/11/2018
5. | Ñôn vò yeâu caàu/Custommer |  |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM AN GIANG
| Ñòa chæ/ Address |  |  |  |  | : | Quoác loä 91, phöôøng Myõ Thôùi, TP.Long Xuyeân, tænh An Giang
6. | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847:2016
Test method
7. | Ñieàu kieän thöû nghieäm/ Test condition:
- Maãu ñöôïc thöû nghieäm taïi Coâng ty Coå phaàn Beâ toâng Ly taâm An Giang,
coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan.
The sample was tested at An Giang Centrifuged Concrete Joint Stock Company,
with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
- Coät ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: 02/14-PC-11.0/ACECO/07-17 cuûa Coâng ty
Coå phaàn Beâ toâng Ly taâm An Giang
Electrical pole was produced based on the designed drawing No. 02/14-PC-11.0/ACECO/07-17
of An Giang Centrifuged Concrete Joint Stock Company
8. | Thieát bò thöû nghieäm chính/Main equipment for testing:
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm/ Tape rule 20 m, measuring range 1 mm
- Thöôùc caëp, vaïch chia 0,02 mm/ Vernier caliper, division 0,02 mm
- Boä caên laù 0.02 ñeán 1.00 mm/ Feeler gauge range 0.02 to 1.00 mm
- Kính phoùng ñaïi 4 mm, vaïch chia 0,02 mm
Graduated microscope, measuring range 4mm, division of 0,05 mm
Ngöôøi thöïc hieän | [6 empty] | Phoøng TN |  |  | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory |  |  | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyeãn Vaên Hoàng Chi |  |  | Nguyeãn Thò Thuûy
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [13 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [6 empty] | LAS-XD 506
1108-172
Ngaøy/Date: |  | 08/11/2018 |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [6 empty] | Trang 2/2
9. | Keát quaû thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics |  |  |  | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  | Ñaùnh giaù Comments
1 | 14-PC-11.0, Số 04-10/2018 |  |  | 1. Kích thöôùc/ Dimension |  |  |  | mm
|  |  |  | - | Chieàu daøi/ Length |  |  |  | 14000 (+25;-10) |  | 14000 |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh |  |  |  | 190 (+4;-2) |  | 191
Outside diameter at top
|  |  |  | - | Chieàu daøy ñænh |  |  |  | 60 (+7;-5) |  | 61
Wall-thickness at top
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy |  |  |  | 377 (+4;-2) |  | 378
Outside diameter at bottom
|  |  |  | - | Chieàu daøy ñaùy |  |  |  | 80 (+7;-5) |  | 82
Wall-thickness at bottom
|  |  |  | 2. | Kích thöôùc cuûa loã roã |  |  | mm |  |  |  |  | Ñaït/ Pass
Dimension of skin hole
[5 empty] | Ñöôøng kính/ diameter |  |  |  | Max 10 |  | Nhaün, khoâng roã
[5 empty] | Chieàu saâu/ depth |  |  |  | Max 5
|  |  |  | 3. | Kích thöôùc cuûa u cuïc boä (chieàu cao) veát loõm (chieàu saâu) |  |  | mm | Max 2 |  | Nhaün, khoâng loõm |  | Ñaït/ Pass
Dimension of partial (height) dent
|  |  |  | 4. | Nöùt beà maët/ Surface cracking |  |  | mm | Max 0,05 |  | Khoâng nöùt |  | Ñaït/ Pass
10. | Nhaän xeùt/ Comments:
Caên cöù tieâu chuaån TCVN 5847 : 2016 vaø baûn veõ thieát keá coätï ñieän 14 m cuûa Coâng ty Coå phaàn
Beâ toâng Ly taâm An Giang. Keát quaû thöû nghieäm cho thaáy:
Based on TCVN 5847: 2016 and designed drawing for Electricad pole type 14 m of An Giang
Centrifuged Concrete Joint Stock Company, the above test result of the tested pole show that:
| - Kích thöôùc coät ñieän | [6 empty] | : Ñaït yeâu caàu/ Pass
Pole dimension
| - Kích thöôùc cuûa loã roã | [6 empty] | : Ñaït yeâu caàu/ Pass
Dimension of skin hole
| - Kích thöôùc cuûa u cuïc boä (chieàu cao) veát loõm | [6 empty] | : Ñaït yeâu caàu/ Pass
Dimension of partial (height) dent
| - Nöùt beà maët/ Cracking surface: | [6 empty] | : Ñaït yeâu caàu/ Pass
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [13 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only