## COT TRON
1 | 2 |  | 3 | 4 | [7 empty] | 5 | 6 |  | 7 | 8 | 9 | 10
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [8 empty] | LAS-XD 506
1027-04
Ngaøy/Date: |  | 27/10/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse, 3 copies | [8 empty] | Trang 1/2
1. | Ñôn vò yeâu caàu/ Client |  |  |  |  | : | COÂNG TY COÅ PHAÀN CÔ KHÍ KIEÂN GIANG(KIMEC) .
2 | Khaùch haøng/ Custommer |  |  |  |  | : | COÂNG TY ÑIEÄN LÖÏC BEÁN TRE.
3 | Ñòa chæ / Address |  |  |  |  | : | SOÁ 181 CMT8,PHÖÔØNG VÓNH LÔÏI ,TP RAÏCH GIAÙ, TÆNH KIEÂN GIANG.
4 | Coâng trình/ Project |  |  |  |  | : | GOÙI THAÀU:THI COÂNG XAÂY DÖÏNG COÂNG TRÌNH GOÙI 1-G1 THUOÄC COÂNG TRÌNH:BOÏC HOÙA LÖÔÙI 22KV HUYEÄN BÌNH ÑAÏI NAÊM 2018 KHU VÖÏC 1,BOÏC HOÙA LÖÔÙI 22KV HUYEÄN BÌNH ÑAÏI KHU VÖÏC 2,BOÏC HOÙA LÖÔÙI TRUNG THEÁ HUYEÄN CHAÂU THAØNH NAÊM 2018 VUØNG 2.
5 | Teân Maãu |  |  |  |  | : | M02-PC.I-12-190-7.2.TCVN 5847:2016.
| Name of sample | [5 empty] | Prestressed centrifugal concrete electrical pole
6 | Kyù hieäu maãu |  |  |  |  | : | Xem trang sau :(2/2)
Code of sample
7 | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 truï/ poles.
8 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847:2016;TCVN 9334-2012.
Test method
9 | Yeâu caàu thöû nghieäm |  |  |  |  | : | Ño kích thöôùc,ngoaïi quan.
Test requirement
10 | Ngaøy thí nghieäm |  |  |  |  | : | 25/10/2018.
Testing date
11 | Ñieàu kieän thöû nghieäm
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
Tape rule 20 m, measuring range 1 mm
- Thöôùc caëp, vaïch chia 0,02 mm
Vernier caliper, division 0,02 mm
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
Graduated microscope, measuring range 4 mm, division of 0,05 mm.
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: KIMEC TA-12-7.2-2 ,thaùng 01/2018 cuûa COÂNG TY COÅ PHAÀN CÔ KHÍ KIEÂN GIANG (KIMEC). Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing No: KIMEC TA 12-7.2-2; 01/2018 of KIEN GIANG MECHANIC JOINT STOCK COMPANY (KIMEC JSC).
Ngöôøi thöïc hieän | [6 empty] | Tröôûng Phoøng TN |  |  |  | P.Giaùm Ñoác
Tested By | [6 empty] | Chief of Laboratory |  |  |  | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyeãn Vaên Hoàng Chi |  |  |  | Nguyeãn Thò Thuûy
1. Caùc keát quûa thöû nghieäm ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
1027-04 |  |  |  |  | PHUÏ LUÏC KEÁT QUAÛ THÖÛ NGHIEÄM | [10 empty] | LAS-XD 506
Ngaøy/ Date: |  | 27/10/2018. |  |  | KEÁT QUAÛ THÖÛ NGHIEÄM | [10 empty] | Trang 2/2
Teân chæ tieâu |  |  |  |  | Chieàu daøi (mm) |  |  | Chieàu daøy taïi ñænh(mm) | Chieàu daøy taïi ñaùy(mm) | Ñöôøng kính ngoaøi taïi ñænh(mm) | [5 empty] | Ñöôøng kính ngoaøi taïi ñaùy(mm)
Möùc chæ tieâu chaát löôïng thieát keá vaø theo TCVN 5847 : 2016 |  |  |  |  | 12000 +25,-10 |  |  | 50 +7-5 | 60 +7-5 | 190 +4;-2 | [5 empty] | 350 +4-2
M02-PC.I-12-190-7.2.TCVN 5847:2016.
|  | M02 |  |  | 12005 |  |  | 54 | 64 | 192 | [5 empty] | 352
12 | Nhaän xeùt/ Comments |  |  |  |  | :
Döïa theo tieâu chuaån 5847 : 2016 ;Theo Yeâu caàu kyõ thuaät cuûa Hôïp Ñoàng vaø baûn veõ thieát keá truï ñieän PC.I-12-190-7.2-2 ,Thaùng 01/2018 cuûa COÂNG TY COÅ PHAÀN CÔ KHÍ KIEÂN GIANG(KIMEC). Keát quaû thöû nghieäm truï ñieän cho thaáy :
Based on TCVN 5847:2018 ; Contracs Technical Requirement and designed drawing for PCRC Electricad pole type PC.I-12-190-7.2-2; 01/2018 result of KIEN GIANG MECHANIC JSC(KIMEC),the above test result of the tested pole show that:
| -Kích thöôùc truï ñieän/ Pole Dimension : | [7 empty] | Ñaït yeâu caàu/ Pass
1. Caùc keát quûa thöû nghieäm ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0