## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1108-176
Ngaøy/Date: |  | 08/11/2018. |  |  | Ban haønh laàn 1, soá baûn 03 / The 1st isuse, 03 copies | [9 empty] | Trang 1/3
1 | Teân Maãu/Sample name |  |  |  |  | : | COÄT ÑIEÄN BTCT LY TAÂM ÖÙNG LÖÏC TRÖÔÙC TH-PC.I-7,5-160-3.0. TCVN 5847:2016
2 | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 truï / pole
3 | Ngaøy thöû/Testing date |  |  |  |  | : | 05/11/2018.
4 | Chuû Ñaàu Tö/Proj.Investor |  |  |  |  | : | -
5 | Nhaø Thaàu/Contractor |  |  |  |  | : | -
6 | Ñôn vò yeâu caàu/Custommer |  |  |  |  | : | COÂNG TY TNHH XAÂY LAÉP ÑIEÄN HOAØNG PHAÙT
7 | Ñòa chæ / Address |  |  |  |  | :
8 | Coâng trình/ Project |  |  |  |  | : | THI COÂNG XAÂY DÖÏNG COÂNG TRÌNH:CAÛI TAÏO ÑÖÔØNG DAÂY TRUNG AÙP TUYEÁN 478NP ÑOAÏN TÖØ R-NPHÖÔÙC ÑEÁN TRAÏM TAÂN ÑÖÙC 3.
9 | Ñòa ñieåm / Project Add. |  |  |  |  | : | TÆNH NINH THUAÄN.
10 | Kyù hieäu maãu/ |  |  |  |  | : | TH-PC.1-7.5-160-3.0-K2-TCVN 5847:2016 - HP.05.11
Code of sample
11 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847:2016.
Test method
12 | Ñieàu kieän thöû nghieäm
Maãu ñöôïc thöû nghieäm taïi nhaø maùy :Thoân Ñoâng Thuaän, Xaõ Taân Haø,Huyeän Haøm Taân- Tænh Bình Thuaän , coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan. The sample was tested at Factory - of Taân Haø Company Co,.Ltd, with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá : | [6 empty] | 50 | MPa
Concrete with design grade :
| - Thöû keùo ñaàu truï danh ñònh Pn: kN | [8 empty] | 3 | 306 | kGf
Nominal load test at the top of pole :
| - Thöû keùo ñaàu truï danh ñònh Pu: K=: kN | [8 empty] | 6 | 612 | kGf
Breaking Load test at the top of pole : Pu max
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: DECO-14HT-XD.05 , cuûa COÂNG TY COÅ PHAÀN THEÁT KEÁ VAØ XAÂY DÖÏNG ÑAÏT HOAØNG. Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing No: DECO -14-HT-XD.05 , of DAT HOANG DESIGN & CONSTRUCTION JSC .
Ngöôøi thöïc hieän | [6 empty] | Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyeãn Vaên Hoàng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1108-176
Ngaøy/Date: |  | 08/11/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây:
The test was carried out as the sketch below
Sketch for tensile load test at the the top of pole
13 | Thieát bò thöû nghieäm chính:
Main equipment fo testing
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
Tape rule 20 m, measuring range 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) MPa, type N
- Löïc keá coù thang ño 2000 kgf, vaïch chia 01 kgf.
Dynamometer measuring range 2000 kgf, division 0.1 kgf.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
Graduated microscope, measuring range 4mm, division of 0,05mm.
- Boä caên laù 0.02 ñeán 1.00 mm.
Feeler gauge range 0.02 to 1.00 mm.
14 | Keát quaû thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  |  | Ñaùnh giaù Comments
1 | TH-PC.1-7.5-160-3.0-K2-TCVN 5847:2016 - HP.05.11 |  |  | 1. Kích thöôùc/ Dimension | [6 empty] | mm
|  |  |  | - | Chieàu daøi/ Length | [6 empty] | 7500(+25,-10) |  | 7500 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 160 (+4,-2) |  | 162
Outside diameter at top
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 50 (+7;-5) |  | 50
Wall-thickness at top
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 244 (+4,-2) |  | 245
Outside diameter at bottom
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 60 (+7;-5) |  | 61
Wall-thickness at bottom
|  |  |  | 2. Cöôøng ñoä neùn beâ toâng (baèng buùa thöû) | [6 empty] | MPa | min 50 |  | 56 |  |  | Ñaït/ Pass
Estimated Compressive strength of concrete
(concrete Hammer Test)
|  |  |  | 3. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,25 |  | 0 |  |  | Ñaït/ Pass
Width of the maximum crack at Pn
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1108-176
Ngaøy/Date: |  | 08/11/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | TH-PC.1-7.5-160-3.0-K2-TCVN 5847:2016 - HP.05.11 |  |  | 4. Löïc keùo ñaàu truï/ Tensile load at the top pole | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
[12 empty] | 0.75 | 1.5 | 2.25 |  | 3 | Deload
[12 empty] | 76.5 | 153 | 229.5 |  | 306 | 0
|  |  |  | - | Ñoä dòch chuyeån/ Deformation | [5 empty] | mm
|  |  |  | ÔÛ vò trí 1/ at position 1 | [7 empty] | 14 | 30 | 50 |  | 71 | 7
|  |  |  | ÔÛ vò trí 2/ at position 2 | [7 empty] | 6 | 16 | 26 |  | 46 | 4
|  |  |  | ÔÛ vò trí 3/ at position 3 | [7 empty] | 3 | 7 | 12 |  | 23 | 2
|  |  |  | ÔÛ vò trí 4/ at position 4 | [7 empty] | 2 | 4 | 6 |  | 10 | 1
|  |  |  | ÔÛ vò trí 5/ at position 5 | [7 empty] | 0 | 1 | 2 |  | 3 | 0
|  |  |  | - | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks
|  |  |  | .- | Soá löôïng veát nöùt noái tieáp voøng quanh thaân truï | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks,continuous on the pole.
|  |  |  | - | Beà roäng cuûa veát nöùt lôùn nhaát, | [5 empty] | mm | 0 | 0 | 0 |  | 0 | 0
Width of the maximum cracks
|  |  |  | - | Löïc keùo tôùi haïn Pu; K=2 | [5 empty] | KN (kGf) | TRUÏ CHÖA PHAÙ HUÛY KHI K=2=Pu=6.0 kN (612 kGf)
Breaking Load Pmax
15 | Nhaän xeùt/ Comments |  |  |  |  | :
Caên cöù tieâu chuaån 5847 : 2016 vaø baûn veõ thieát keá truï ñieän 7.5M-F300 ; cuûa COÂNG TY COÅ PHAÀN THIEÁT KEÁ VAØ XAÂY DÖÏNG ÑAÏT HOAØNG .Keát quaû thöû nghieäm cho thaáy :
Based on TCVN 5847: 2016 and designed drawing for PCRC Electricad pole type 7.5 M-F300 ; result of DATHOANG design & CONSTRUCTION JSC,the above test result of the tested pole show that:
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
Dimension
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
Grade of concrete
| - Thöû löïc keùo ñaàu truï | [7 empty] | : | Ñaït yeâu caàu/ Pass
Tensile load at the top of pole test
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
L=7500
1300
1500
1500
1500
1500
250