## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0814-03
Ngaøy/Date: |  | 14/8/2018. |  |  | Ban haønh laàn 1, soá baûn 04/ The 1st isuse,04 copies | [9 empty] | Trang 1/3
1 | Teân Maãu/Sample name |  |  |  |  | : | TRUÏ ÑIEÄN BTLT TIEÀN AÙP-Loaïi 14m-8.5kN (867 kGf),K=2.
2 | Soá löôïng maãu/Quantity |  |  |  |  | : | 01 truï / pole
3 | Ngaøy thöû/Testing date |  |  |  |  | : | 10/8/2018.
4 | Khaùch haøng/Custommer |  |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG BIEÂN HOØA.
COÂNG TY ÑIEÄN LÖÏC BAØ RÒA VUÕNG TAØU.
5 | Ñòa chæ / Address |  |  |  |  | : | ÑÖÔØNG SOÁ 1-KCN BIEÂN HOØA 1-P AN BÌNH-TP BIEÂN HOØA-TÆNH ÑOÀNG NAI
6 | Coâng trình/ Project |  |  |  |  | : | XDM,CAÛI TAÏO NAÂNG CAÁP ÑÖÔØNG DAÂY TRUNG THEÁ VAØ TRAÏM BIEÁN AÙP PHUÏC VUÏ KHU NUOÂI TROÀNG THUÛY HAÛI SAÛN TAÄP TRUNG HUYEÄN ÑAÁT ÑOÛ,XUYEÂN MOÄC,TÆNH BAØ RÒA - VUÕNG TAØU.
7 | Kyù hieäu maãu/ |  |  |  |  | : | PC.I-14-190-8.5kN-TCVN 5847-2016,K=2 - Soá SX: T 7/2018.
Code of sample
8 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847:2016; TCVN 9334:2012.
Test method
9 | Ñieàu kieän thöû nghieäm
Maãu ñöôïc thöû nghieäm taïi Nhaø Maùy saûn xuaát cuûa Coâng Ty Coå Phaàn Beâ Toâng Bieân Hoøa, coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan. The sample was tested at Workshop -Bieân Hoøa Joint Sock Company , with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá : | [6 empty] | 60 | MPa
Concrete with design grade :
| - Thöû keùo ñaàu truï danh ñònh Pn: kN | [8 empty] | 8.5 | 867 | (kGf)
Nominal load test at the top of pole :
| - Thöû keùo ñaàu truï Phaù huûy K=2.0: | [7 empty] | kN | 17 | 1734 | ( kGf)
Breaking Load test at the top of pole : Pu
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: CÑTA-14m-8.5-N2 ,thaùng 11/2017 cuûa COÂNG TY COÅ PHAÀN BEÂ TOÂNG BIEÂN HOØA. Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing No: CÑTA-14m-8.5-N2; 11/2017 of BIEÂN HOØA CONCRETE JSC..
Ngöôøi thöïc hieän | [6 empty] | Tröôûng Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyễn Văn Hồng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc keát KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0814-03
Ngaøy/Date: |  | 14/8/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây:
The test was carried out as the sketch below
Sketch for tensile load test at the the top of pole
10 | Thieát bò thöû nghieäm chính:
Main equipment fo testing
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
Tape rule 20 m, measuring range 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) MPa, type N
- Löïc keá coù thang ño 3000 kgf, vaïch chia 01 kgf.
Dynamometer measuring range 3000 kgf, division 01 kgf.
- Boä caên laù töø 0.02 ñeán 1.00 mm.
Feeler gauge range 0.02mm to 1.00 mm.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
Graduated microscope, measuring range 4mm, division of 0,05mm.
11 | Keát quaû thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  |  | Ñaùnh giaù Comments
1 | PC.I-14-190-8.5kN-TCVN 5847-2016,K=2 - Soá SX: T 7/2018. |  |  | 1. Kích thöôùc/ Dimension | [6 empty] | mm
|  |  |  | - | Chieàu daøi/ Length | [6 empty] | 14000(±25,-10) |  | 14000 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 190 (+4,-2) |  | 192
Outside diameter at top
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 50 (+7;-5) |  | 55
Wall-thickness at top
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 380 (+4,-2) |  | 380
Outside diameter at bottom
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 60 (+7;-5) |  | 64
Wall-thickness at bottom
|  |  |  | 2. Cöôøng ñoä neùn beâ toâng öôùc tính (baèng buùa thöû) | [6 empty] | MPa | min 60 |  | 61 |  |  | Ñaït/ Pass
Compressive strength of concrete
(Estimated for Hammer Test)
|  |  |  | 3. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,25 |  | 0.05 |  |  | Ñaït/ Pass
Width of the maximum crack at Pn
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0814-03
Ngaøy/Date: |  | 14/8/2018. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | PC.I-14-190-8.5kN-TCVN 5847-2016,K=2 - Soá SX: T 7/2018. |  |  | 4. Löïc keùo ñaàu truï / Tensile load at the top pole | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
[12 empty] | 2.125 | 4.25 | 6.375 |  | 8.5 | Deload
[11 empty] | kGf | 216.75 | 433.5 | 650.25 |  | 867
|  |  |  | - | Ñoä dòch chuyeån/ Deformation | [5 empty] | mm
|  |  |  | ÔÛ vò trí 1/ at position 1 | [7 empty] | 86 | 188 | 257 |  | 374 | 36
|  |  |  | ÔÛ vò trí 2/ at position 2 | [7 empty] | 47 | 107 | 140 |  | 233 | 24
|  |  |  | ÔÛ vò trí 3/ at position 3 | [7 empty] | 26 | 66 | 94 |  | 131 | 10
|  |  |  | ÔÛ vò trí 4/ at position 4 | [7 empty] | 8 | 25 | 48 |  | 72 | 4
|  |  |  | ÔÛ vò trí 5/ at position 5 | [7 empty] | 2 | 4 | 6 |  | 10 | 1
|  |  |  | - | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 10 | 0
Quantity of the visual cracks
|  |  |  | .- | Soá löôïng veát nöùt noái tieáp voøng quanh thaân truï | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks,continuous on the pole.
|  |  |  | - | Beà roäng cuûa veát nöùt lôùn nhaát, | [5 empty] | mm | 0 | 0 | 0 |  | 0.05 | 0
Width of the maximum cracks
|  |  |  | - | Löïc keùo tôùi haïn Pu (K=2.0) | [5 empty] | kN (kGf) | Pu = 17.0 kN (1734 kGf) ,truï chöa bò phaù huûy.
Breaking Load Pu (max)
12 | Nhaän xeùt/ Comments |  |  |  |  | :
Caên cöù tieâu chuaån 5847:2016 vaø baûn veõ thieát keá truï ñieän 14m-8.5-N2; 11/2017 cuûa COÂNG TY COÅ PHAÀN BEÂ TOÂNG BIEÂN HOØA.Keát quaû thöû nghieäm truï ñieän cho thaáy :
Based on TCVN 5847:2016 and designed drawing for PCRC Electricad pole type 14m-8.5-N2; 11/2017 result of BIEÂN HOØA CONCRETE JSC,the above test result of the tested pole show that:
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
Dimension
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
Grade of concrete
| - Thöû löïc keùo ñaàu truï | [7 empty] | : | Ñaït yeâu caàu/ Pass
Tensile load at the top of pole test
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
L=14000
2400
2800
2800
2800
2800
250