## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0718-02
Ngaøy/Date: |  | 18/7/2019. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 1/3
1 | Teân Maãu/Sample name |  |  |  |  | : | TRUÏ ÑIEÄN VIEÃN THOÂNG BTLT ÖÙNG LÖÏC TRÖÔÙC 8.A-R-65.II (420 KGF).
2 | Soá löôïng maãu/Quantity |  |  |  |  | : | 01 truï / pole
3 | Ngaøy thöû/Testing date |  |  |  |  | : | 16/7/2019.
4 | Ñôn vò cung caáp/Provider |  |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM HAÄU GIANG.
5 | Ñòa chæ / Address |  |  |  |  | : | ÑÖÔØNG SOÁ 2-CUÏM CN-TTCN PHÖÔØNG 7-TP. VÒ THANH-TÆNH HAÄU GIANG.
6 | Chuû Ñaàu Tö / Investmen
7 | Coâng trình/ Project |  |  |  |  | :
8 | Kyù hieäu maãu/Sample code |  |  |  |  | : | 8.A-R-65.II- Soá : M 02-T 06/2019.
9 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | TCCS : 01-2009/VNPT;TK TCVN 5847:2016;VAØ THEO YEÂU CAÀU KHAÙCH HAØNG.
Test method
10 | Ñieàu kieän thöû nghieäm
Maãu ñöôïc thöû nghieäm taïi Nhaø maùy thuoäc COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM HAÄU GIANG , coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan. The sample was tested at Workshop - HAÄU GIANG CENTRIFUGED CONCRETE JOINT STOK COMPANY , with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá : | [6 empty] | 40 | MPa
Concrete with design grade :
| - Thöû keùo ñaàu truï danh ñònh Pn: kN | [8 empty] | 3.43 | 349.86 | (kGf)
Nominal load test at the top of pole :
| - Thöû keùo ñaàu truï Phaù huûy K=1.2: | [7 empty] | kN | 4.116 | 419.832 | ( kGf)
Breaking Load test at the top of pole : Pu
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá: 8.A-R-65.II, cuûa TAÄP ÑOAØN BÖU CHÍNH VIEÃN THOÂNG VIEÄT NAM (VNPT). Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing : 8.A-R-65.II of VNPT .
Ngöôøi thöïc hieän | [6 empty] | Tröôûng Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyễn Văn Hồng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc keát KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0718-02
Ngaøy/Date: |  | 18/7/2019. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây:
The test was carried out as the sketch below
Sketch for tensile load test at the the top of pole
11 | Thieát bò thöû nghieäm chính:
Main equipment for testing
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
Tape rule 20 m, measuring range 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) MPa, type N
- Löïc keá coù thang ño 2000 kgf, vaïch chia 01 kgf.
Dynamometer measuring range 2000 kgf, division 01 kgf.
- Boä caên laù töø 0.02 ñeán 1.00 mm.
Feeler gauge range 0.02mm to 1.00 mm.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
Graduated microscope, measuring range 4mm, division of 0,05mm.
12 | Keát quaû thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  |  | Ñaùnh giaù Comments
1 | 8.A-R-65.II- Soá : M 02-T 06/2019. |  |  | 1. Kích thöôùc/ Dimension | [6 empty] | mm
|  |  |  | - | Chieàu daøi/ Length | [6 empty] | 8000  15 |  | 8005 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 160  3 |  | 161
Outside diameter at top
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 50  2 |  | 51
Wall-thickness at top
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 250  3 |  | 252
Outside diameter at bottom
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 55  2 |  | 56
Wall-thickness at bottom
|  |  |  | 2. Cöôøng ñoä neùn beâ toâng (baèng buùa thöû) | [6 empty] | MPa | min 40 |  | 44 |  |  | Ñaït/ Pass
Compressive strength of concrete
(for Hammer Test)
|  |  |  | 3. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | N/A |  | 0.05 |  |  | Ñaït/ Pass
Width of the maximum crack at Pn
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0718-02
Ngaøy/Date: |  | 18/7/2019. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | 8.A-R-65.II- Soá : M 02-T 06/2019. |  |  | 4. Löïc keùo ñaàu truï / Tensile load at the top pole | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
[12 empty] | 0.8575 | 1.715 | 2.5725 |  | 3.43 | Deload
[11 empty] | kGf | 87.465 | 174.93 | 262.395 |  | 349.86
|  |  |  | - | Ñoä dòch chuyeån/ Deformation | [5 empty] | mm
|  |  |  | ÔÛ vò trí 1/ at position 1 | [7 empty] | 37 | 74 | 136 |  | 251 | 13
|  |  |  | ÔÛ vò trí 2/ at position 2 | [7 empty] | 21 | 30 | 75 |  | 109 | 9
|  |  |  | ÔÛ vò trí 3/ at position 3 | [7 empty] | 9 | 16 | 33 |  | 65 | 6
|  |  |  | ÔÛ vò trí 4/ at position 4 | [7 empty] | 5 | 9 | 17 |  | 31 | 3
|  |  |  | ÔÛ vò trí 5/ at position 5 | [7 empty] | 1 | 3 | 5 |  | 12 | 1
|  |  |  | - | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 14 | 0
Quantity of the visual cracks
|  |  |  | .- | Soá löôïng veát nöùt noái tieáp voøng quanh thaân truï | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks,continuous on the pole.
|  |  |  | - | Beà roäng cuûa veát nöùt lôùn nhaát, | [5 empty] | mm | 0 | 0 | 0 |  | 0.05 | 0
Width of the maximum cracks
|  |  |  | - | Löïc keùo tôùi haïn Pu (K=1.2) | [5 empty] | kN (kGf) | TRUÏ CHÖA PHAÙ HUÛY KHI Pu=K1.2=4.12 KN (420 KGF).
Breaking Load Pu (max)
13 | Nhaän xeùt/ Comments |  |  |  |  | :
Caên cöù tieâu chuaån TCCS:01/2009 VNPT vaø baûn veõ thieát keá truï ñieän 8.A-R-65.II ; cuûa TAÄP ÑOAØN BÖU CHÍNH VIEÃN THOÂNG VIEÄT NAM (VNPT) .Keát quaû thöû nghieäm truï ñieän cho thaáy :
Based on TCCS:01/2009 VNPT and designed drawing for PCRC Electricad pole type 8.A-R-65.II; result of VNPT,the above test result of the tested pole show that:
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
Dimension
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
Grade of concrete
| - Thöû löïc keùo ñaàu coät | [7 empty] | : | Ñaït yeâu caàu/ Pass
| Tensile load at the top of pole test | [7 empty] | :
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
L=8000
1100
1600
1600
1600
1600
100