## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0522-04
Ngaøy/Date: |  | 22/5/2020. |  |  | Ban haønh laàn 1, soá baûn 03 / The 1st isuse, 03 copies | [9 empty] | Trang 1/3
1 | Teân Maãu/Sample name |  |  |  |  | : | TRUÏ ÑIEÄN BEÂ TOÂNG LY TAÂM TIEÀN AÙP-Loaïi 18m-190-10.0 kN-K=1.5.
2 | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 truï / pole
3 | Ngaøy thöû/Testing date |  |  |  |  | : | 22/5/2020.
4 | Chuû Ñaàu Tö/Proj.Investor |  |  |  |  | :
5 | Nhaø Thaàu/Contractor |  |  |  |  | :
6 | Ñôn vò yeâu caàu/Custommer |  |  |  |  | : | COÂNG TY TNHH BEÂ TOÂNG LY TAÂM MIEÀN ÑOÂNG.
7 | Ñòa chæ / Address |  |  |  |  | : | SOÁ 7/7B-ÑT 747-BUØI THÒ XUAÂN-TAÂN PHÖÔÙC-TAN BÌNH-DÓ AN -T. BÌNH DÖÔNG.
8 | Coâng trình/ Project |  |  |  |  | :
9 | Ñòa ñieåm / Project Add. |  |  |  |  | :
10 | Kyù hieäu maãu/Sample Code |  |  |  |  | : | MÑ-PC.I-18-190-10.0 KN-K=1.5- Soá M01 - NSX T 4/2020.
11 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | TCVN 5847: 2016 VAØ THEO YEÂU CAÀU KHAÙCH HAØNG.
Test method
12 | Ñieàu kieän thöû nghieäm
Maãu ñöôïc thöû nghieäm taïi nhaø maùy : soá 7/7 B,Buøi Thò Xuaân,Taân Phöôùc,Taân Bình- Dó An- Tænh Bình Döông, coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan. The sample was tested at Factory - of Mien Dong Company Ltd, with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá : | [6 empty] | 40 | MPa
Concrete with design grade :
| '- Thöû keùo ñaàu truï danh ñònh Pn : | [7 empty] | KN | 10 | 1020 | kGf
Nominal load test at the top of pole :
| '- Thöû keùo ñaàu truï Phaù Huûy:Pu:K 1.5 | [7 empty] | KN | 15 | 1530 | kGf
Breaking Load test at the top of pole : Pu max
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: TTCBTLT-14 ,thaùng 05/2018 cuûa COÂNG TY CP TÖ VAÁN XAÂY DÖÏNG ÑIEÄN LÖÏC TP. HOÀ CHÍ MINH. Non Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing No: TTC BTLT-14 ,05/2018 of Electrican Construction Consultant HCMC .
Ngöôøi thöïc hieän | [6 empty] | Tröôûng Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyeãn Vaên Hoàng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0522-04
Ngaøy/Date: |  | 22/5/2020. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây:
The test was carried out as the sketch below
MAËT BÍCH NOÁI TRUÏ
13 | Thieát bò thöû nghieäm chính:
Main equipment for testing
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
Tape rule 20 m, measuring range 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) MPa, type N
- Löïc keá coù thang ño 3000 kgf, vaïch chia 01 kGf.
Dynamometer measuring range 3000 kgf, division 01 kGf.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
Graduated microscope, measuring range 4mm, division of 0,05mm.
- Boä caên laù 0.02 ñeán 1.00 mm.
Feeler gauge range 0.02 to 1.00 mm.
14 | Keát quaû thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  |  | Ñaùnh giaù Comments
1 | MÑ-PC.I-18-190-10.0 KN-K=1.5- Soá M01 - NSX T 4/2020. |  |  | 1. Kích thöôùc/ Dimension | [6 empty] | mm
|  |  |  | - | Chieàu daøi/ Length | [6 empty] | 18000(+50;-10) |  | 18015 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 190 (+4;-2) |  | 191
Outside diameter at top
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 60 (+7;-5) |  | 61
Wall-thickness at top
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 430 (+4;-2) |  | 432
Outside diameter at bottom
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 75 |  | 80
Wall-thickness at bottom
|  |  |  | 2. Cöôøng ñoä neùn beâ toâng (baèng buùa thöû) | [6 empty] | MPa | min 40 |  | 60 |  |  | Ñaït/ Pass
Compressive strength of concrete
(concrete Hammer Test)
|  |  |  | 3. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,25 |  | 0.05 |  |  | Ñaït/ Pass
Width of the maximum crack at Pn
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0522-04
Ngaøy/Date: |  | 22/5/2020. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | MÑ-PC.I-18-190-10.0 KN-K=1.5- Soá M01 - NSX T 4/2020. |  |  | 4. Löïc keùo ñaàu truï/ Tensile load at the top pole | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
[12 empty] | 2.5 | 5 | 7.5 |  | 10 | Deload
[12 empty] | 255 | 510 | 765 |  | 1020 | 0
|  |  |  | - | Ñoä dòch chuyeån/ Deformation | [5 empty] | mm
|  |  |  | ÔÛ vò trí 1/ at position 1 | [7 empty] | 81 | 180 | 380 |  | 692 | 56
|  |  |  | ÔÛ vò trí 2/ at position 2 | [7 empty] | 42 | 116 | 229 |  | 376 | 34
|  |  |  | ÔÛ vò trí 3/ at position 3 | [7 empty] | 26 | 65 | 137 |  | 197 | 14
|  |  |  | ÔÛ vò trí 4/ at position 4 | [7 empty] | 12 | 24 | 52 |  | 87 | 7
|  |  |  | ÔÛ vò trí 5/ at position 5 | [7 empty] | 2 | 6 | 11 |  | 21 | 2
|  |  |  | - | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 29 | 0
Quantity of the visual cracks
|  |  |  | .- | Soá löôïng veát nöùt noái tieáp voøng quanh thaân truï | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks,continuous on the pole.
|  |  |  | - | Beà roäng cuûa veát nöùt lôùn nhaát, | [5 empty] | mm | 0 | 0 | 0 |  | 0.05 | 0
Width of the maximum cracks
|  |  |  | - | Löïc keùo tôùi haïn Pu; k=1.5 | [5 empty] | KN (kGf) | TRUÏ CHÖA PHAÙ HUÛY KHI Pu=15.0 kN (1530 kGf)
Breaking Load Pmax
15 | Nhaän xeùt/ Comments |  |  |  |  | :
Caên cöù tieâu chuaån 5847:2016 vaø baûn veõ thieát keá truï ñieän PC.I-18-190-10.0-k1.5; 05/2018 cuûa COÂNG TY COÅ PHAÀN TÖ VAÁN XAÂY DÖÏNG ÑIEÄN LÖÏC TP.HOÀ CHÍ MINH.Keát quaû thöû nghieäm cho thaáy :
Based on TCVN 5847: 2016 and designed drawing for PCRC Electricad pole type PC.I-18-190-10.0-K1.5; 05/2018 result of HCMC POWER CONSTRUCTION CONSULTANT JSC ,the above test result of the tested pole show that:
| - Ngoaïi Quan,Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
Ouside Dimension
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
Grade of concrete
| - Thöû löïc keùo ñaàu truï | [7 empty] | : | Ñaït yeâu caàu/ Pass
Tensile load at the top of pole test
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
L=18000
3000
3600
3600
3600
3600
250