## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1028-01
Ngaøy/Date: |  | 28/10/2020. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 1/3
1 | Teân Maãu/Sample name |  |  |  |  | : | TRUÏ ÑIEÄN BTLT DÖÏ ÖÙNG LÖÏC-Loaïi :16m-9.2 KN (938 kGf),K=2.
2 | Soá löôïng maãu/Quantity |  |  |  |  | : | 01 truï / pole
3 | Ngaøy thöû/Testing date |  |  |  |  | : | 23/10/2020.
4 | Khaùch haøng/Custommer |  |  |  |  | : | COÂNG TY TNHH SAÛN XUAÁT TRUÏ ÑIEÄN VAØ CÔ KHÍ TIEÀN PHONG.
COÂNG TY ÑIEÄN LÖÏC BÌNH DÖÔNG.
5 | Ñòa chæ / Address |  |  |  |  | : | 36 ÑIEÄN BIEÂN PHUÛ-PHÖÔØNG 15-QUAÄN BÌNH THAÏNH-TP.HOÀ CHÍ MINH.
6 | Coâng trình/ Project |  |  |  |  | : | "CAÙC LOÄ RA 22 kV TBA 110 kV VSIP II MÔÛ ROÄNG 2".
7 | Kyù hieäu maãu/ |  |  |  |  | : | PC-16-9.2 KN-K=2-Soá: 2930 .
Code of sample
8 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | TCVN 5847:2016; Vaø Theo yeâu caàu Khaùch haøng.
Test method
9 | Ñieàu kieän thöû nghieäm
Maãu ñöôïc thöû nghieäm taïi Xöôûng saûn xuaát Soá 02 :C14/24,QL 1A,AÁp 3,Xaõ Taân Kieân,Huyeän Bình Chaùnh- Tp HCM, coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan. The sample was tested at Workshop -Tien Phong Company Ltd., No 02:C14/24,QL1A,Hamlet No 3,Tan Kien Ward, Binh Chanh District, Ho Chi Minh City , with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá : | [6 empty] | 50 | MPa
Concrete with design grade :
| - Thöû keùo ñaàu truï danh ñònh Pn: kN | [8 empty] | 9.2 | 938.4 | (kGf)
Nominal load test at the top of pole :
| - Thöû keùo ñaàu truï Phaù huûy K=2: | [7 empty] | kN | 18.4 | 1876.8 | ( kGf)
Breaking Load test at the top of pole : Pu
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: KC-16-920-K2 ,thaùng 04/2019 cuûa COÂNG TY TNHH TÖ VAÁN THIEÁT KEÁ KIEÅM ÑÒNH XAÂY DÖÏNG NAD. Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing No: KC-16-920-K2; 04/2019 of NAD CONSTRUCTION CONSULTANT INSPECTION DESIGN Co,Ltd,.
Ngöôøi thöïc hieän | [6 empty] | Tröôûng Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyễn Văn Hồng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc keát KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1028-01
Ngaøy/Date: |  | 28/10/2020. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
10 | Thieát bò thöû nghieäm chính:
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
- Löïc keá coù thang ño 2000 kgf, vaïch chia 01 kgf.
- Boä caên laù töø 0.02 ñeán 1.00 mm.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
11 | Keát quaû Thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû TN Test result |  |  | Ñaùnh giaù Comments
1 | PC-16-9.2 KN-K=2-Soá: 2930 . |  |  | 1 | Chieàu daøy lôùp beâ toâng vaø vöõa | [5 empty] | mm
|  |  |  | * | Chieàu daøy lôùp beâ toâng taïi thaân coät | [5 empty] | mm | ≥ 15 |  | 25 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøy lôùp vöõa traùt taïi ñænh | [6 empty] | ≥ 25 |  | 26 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøy lôùp vöõa traùt taïi ñaùy | [6 empty] | ≥ 35 |  | 37 |  |  | Ñaït/ Pass
|  |  |  | 2 | Ñoä nhaün beà maët | [5 empty] | mm
|  |  |  | * | Nhaün ñeàu | [6 empty] | Nhaün ñeàu |  | Nhaün ñeàu |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu saâu loã roã ôû meùp khuoân | [5 empty] | mm | ≤ 2 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøi loã roã ôû meùp khuoân | [6 empty] | ≤ 15 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | 3 | Kích thöôùc loã roã treân maët coät | [5 empty] | mm
|  |  |  | * | Maët ngoaøi | [6 empty] | D ≤ 10 ; L ≤ 5 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | * | Maët muùt coät | [6 empty] | D ≤ 5 ; L ≤ 3 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | * | Veát loài loõm treân thaân coät | [6 empty] | ≤ 2 ; ≤ 2 |  | 0.0 ; 0.0 |  |  | Ñaït/ Pass
|  |  |  | 4 | Nöùt beà maët | [5 empty] | mm
|  |  |  | * | Veát nöùt voøng quanh coät | [6 empty] | 0 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | * | Beà roäng Veát nöùt | [6 empty] | 0.05 ≤ |  | 0 |  |  | Ñaït/ Pass
|  |  |  | 5. Kích thöôùc cô baûn | [6 empty] | mm
|  |  |  | - | Chieàu daøi | [6 empty] | 16000 (+50,-10) |  | 16010 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 190 (+4,-2) |  | 192
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 70 (+7;-5) |  | 68
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 403 (+4,-2) |  | 405
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 85 (+7;-5) |  | 88
|  |  |  | 6.Cöôøng ñoä beâ toâng (baèng buùa thöû). | [6 empty] | MPa | min 50 |  | 61 |  |  | Ñaït/ Pass
|  |  |  | 7. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,25 |  | 0.05 |  |  | Ñaït/ Pass
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
1028-01
Ngaøy/Date: |  | 28/10/2020. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
11.1. | Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây: | [9 empty] | MAËT BÍCH NOÁI TRUÏ
11.2. | KIEÅM TRA LÖÏC GAÂY NÖÙT VAØ LÖÏC PHAÙ HUÛY CUÛA TRUÏ ÑIEÄN.
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | PC-16-9.2 KN-K=2-Soá: 2930 . |  |  | 4. Löïc keùo ñaàu truï / Tensile load at the top pole | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
[12 empty] | 2.3 | 4.6 | 6.9 |  | 9.2 | Deload
[11 empty] | kGf | 234.6 | 469.2 | 703.8 |  | 938.4
|  |  |  | 1 | Ñoä dòch chuyeån | [5 empty] | mm
|  |  |  | * | Ñoä dòch chuyeån ôû vò trí 1 | [6 empty] | 94 | 255 | 411 |  | 631 | 41
|  |  |  | * | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 8 | 0
|  |  |  | * | Beà roäng cuûa veát nöùt lôùn nhaát, (max 0.25mm). | [5 empty] | mm | 0 | 0 | 0 |  | 0.05 | Ñaït
|  |  |  | 2 | Löïc keùo tôùi haïn Pu (K=2) | [5 empty] | kN (kGf) | Pu = 18.4 kN (1877 kGf) ; Truï chöa bò phaù huûy.
12 | Nhaän xeùt/ Comments |  |  |  |  | :
Caên cöù tieâu chuaån 5847 : 2016 vaø baûn veõ thieát keá truï ñieän KC-16-920-K2; 04/2019 cuûa COÂNG TY TNHH TÖ VAÁN THIEÁT KEÁ KIEÅM ÑÒNH XAÂY DÖÏNG NAD.Keát quaû thöû nghieäm cho thaáy:
Based on TCVN 5847:2016 and designed drawing for PCRC Electricad pole type KC-16-920-K2; 04/2019 result of NAD CONSTRUCTION CONSULTANT INSPECTION DESIGN Co.Ltd ,the above test result of the tested pole show that:
| - Ngoaïi quan,Khuyeát taät | [7 empty] | : | Ñaït yeâu caàu/ Pass
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
| - Thöû löïc keùo ñaàu truï | [7 empty] | : | Ñaït yeâu caàu/ Pass
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
L=16000
2500
3200
3200
3200
3200
250