## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0810-02
Ngaøy/Date: |  | 10/8/2021. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 1/3
1 | Ñôn vò yeâu caàu/Custommer |  |  |  |  | : | COÂNG TY TNHH ÑAÀU TÖ TAÂN HAØ.
2 | Ñòa chæ / Address |  |  |  |  | : | THOÂN ÑOÂNG THUAÄN-XAÕ TAÂN HAØ-HUYEÄN HAØM TAÂN-TÆNH BÌNH THUAÄN.
3 | Chuû Ñaàu Tö/Investor |  |  |  |  | : | COÂNG TY ÑIEÄN LÖÏC NINH THUAÄN
4 | Nhaø Thaàu/Contractor |  |  |  |  | : | COÂNG TY TNHH TÖ VAÁN THIEÁT KEÁ ÑIEÄN BAÙCH KHOA.
8 | Coâng trình/ Project |  |  |  |  | : | SÖÛA CHÖÕA LÖÔÙI ÑIEÄN PHAÂN PHOÁI KHU VÖÏC ÑIEÄN LÖÏC THUAÄN NAM NAÊM 2021.
5 | Teân maãu/Sample name |  |  |  |  | : | COÄT ÑIEÄN BEÂ TOÂNG LY TAÂM DÖÏ ÖÙNG LÖÏC-Loaïi: PC.I-12m-190-9.0 kN, K=2,TCVN 5847:2016.
6 | Soá löôïng maãu/Quantity |  |  |  |  | : | 01 truï / pole
7 | Ngaøy thöû/Testing date |  |  |  |  | : | 06/8/2021.
9 | Kyù hieäu maãu/ |  |  |  |  | : | TH-PC.I-12-190-9.0-K2-TCVN 5847:2016-Soá: M 01.
Code of sample
10 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | TCVN 5847:2016; Vaø Theo yeâu caàu Khaùch haøng.
Test method
11 | Ñieàu kieän thöû nghieäm
Maãu ñöôïc thöû nghieäm taïi nhaø maùy :Thoân Ñoâng Thuaän, Xaõ Taân Haø,Huyeän Haøm Taân- Tænh Bình Thuaän , coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan. The sample was tested at Factory - of Taân Haø Company Co,.Ltd, with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá : | [6 empty] | 40 | MPa
Concrete with design grade :
| - Thöû keùo ñaàu truï danh ñònh Pn: kN | [8 empty] | 9 | 918 | (kGf)
Nominal load test at the top of pole :
| - Thöû keùo ñaàu truï Phaù huûy K=2: | [7 empty] | kN | 18 | 1836 | ( kGf)
Breaking Load test at the top of pole : Pu
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: IBST.CÑLTTA.KCCT-03 ,thaùng 3/2018 cuûa VIEÄN KHOA HOÏC COÂNG NGHEÄÏ XAÂY DÖÏNG. Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing No: IBST.CÑLTTA KCCT-02 , 3/2018 of VIETNAM INSTITUTE FOR BUILDING SCIENCE AND TECHNOLOGY .
Ngöôøi thöïc hieän | [6 empty] | Tröôûng Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyễn Văn Hồng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc keát KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0810-02
Ngaøy/Date: |  | 10/8/2021. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
12 | Thieát bò thöû nghieäm chính:
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
- Löïc keá coù thang ño 2000 kgf, vaïch chia 01 kgf.
- Boä caên laù töø 0.02 ñeán 1.00 mm.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
13 | Keát quaû Thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû TN Test result |  |  | Ñaùnh giaù Comments
1 | TH-PC.I-12-190-9.0-K2-TCVN 5847:2016-Soá: M 01. |  |  | 1 | Chieàu daøy lôùp beâ toâng vaø vöõa | [5 empty] | mm
|  |  |  | * | Chieàu daøy lôùp beâ toâng taïi thaân coät | [5 empty] | mm | ≥ 15 |  | 25 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøy lôùp vöõa traùt taïi ñænh | [6 empty] | ≥ 25 |  | 25 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøy lôùp vöõa traùt taïi ñaùy | [6 empty] | ≥ 35 |  | 35 |  |  | Ñaït/ Pass
|  |  |  | 2 | Ñoä nhaün beà maët | [5 empty] | mm
|  |  |  | * | Nhaün ñeàu | [6 empty] | Nhaün ñeàu |  | Nhaün ñeàu |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu saâu loã roã ôû meùp khuoân | [5 empty] | mm | ≤ 2 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøi loã roã ôû meùp khuoân | [6 empty] | ≤ 15 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | 3 | Kích thöôùc loã roã treân maët coät | [5 empty] | mm
|  |  |  | * | Maët ngoaøi | [6 empty] | D ≤ 10 ; L ≤ 5 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | * | Maët muùt coät | [6 empty] | D ≤ 8 ; L ≤ 3 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | * | Veát loài loõm treân thaân coät | [6 empty] | ≤ 2 ; ≤ 2 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | 4 | Nöùt beà maët | [5 empty] | mm
|  |  |  | * | Veát nöùt voøng quanh coät | [6 empty] | 0 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | * | Beà roäng Veát nöùt | [6 empty] | 0.05 ≤ |  | 0 |  |  | Ñaït/ Pass
|  |  |  | 5. Kích thöôùc cô baûn | [6 empty] | mm
|  |  |  | - | Chieàu daøi | [6 empty] | 12000(+25,-10) |  | 12010 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 190 (+4,-2) |  | 191
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 50 (+7;-5) |  | 56
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 380 (+4,-2) |  | 381
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 60 (+7;-5) |  | 67
|  |  |  | 6.Cöôøng ñoä beâ toâng (baèng buùa thöû). | [6 empty] | MPa | min 50 |  | 60 |  |  | Ñaït/ Pass
|  |  |  | 7. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,25 |  | 0.05 |  |  | Ñaït/ Pass
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0810-02
Ngaøy/Date: |  | 10/8/2021. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
13.1. | Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây:
SÔ ÑOÀ THÖÛ KEÙO LÖÏC ÑAÀU TRUÏ
13.2. | KIEÅM TRA LÖÏC GAÂY NÖÙT VAØ LÖÏC PHAÙ HUÛY CUÛA TRUÏ ÑIEÄN.
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | TH-PC.I-12-190-9.0-K2-TCVN 5847:2016-Soá: M 01. |  |  | 4. Löïc keùo ñaàu truï / Tensile load at the top pole | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
[12 empty] | 2.25 | 4.5 | 6.75 |  | 9 | Deload
[11 empty] | kGf | 229.5 | 459 | 688.5 |  | 918
|  |  |  | 1 | Ñoä dòch chuyeån | [5 empty] | mm
|  |  |  | * | Ñoä dòch chuyeån ôû vò trí 1 | [6 empty] | 79 | 188 | 396 |  | 563 | 47
|  |  |  | * | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 19 | 0
|  |  |  | * | Beà roäng cuûa veát nöùt lôùn nhaát, (max 0.25mm). | [5 empty] | mm | 0 | 0 | 0 |  | 0 | Ñaït
|  |  |  | 2 | Löïc keùo tôùi haïn Pu (K=2) | [5 empty] | kN (kGf) | Pu = 18.0 kN (1836 kGf) ; Truï chöa bò phaù huûy.
14 | Nhaän xeùt/ Comments : |  |  |  |  | :
Caên cöù tieâu chuaån 5847:2016 vaø baûn veõ thieát keá truï ñieän 12m-F900; 03/2018 cuûa VIEÄN KHOA HOÏC COÂNG NGHEÄ XAÂY DÖÏNG .Keát quaû thöû nghieäm cho thaáy :
Based on TCVN 5847: 2016 and designed drawing for PCRC Electricad pole type 12m-F900 ; 03/2018 result of VIETNAM INSTITUTE FOR BUILDING SCIENCE AND TECHNOLOGY ,the above test result of the tested pole show that:
| - Ngoaïi quan,Khuyeát taät | [7 empty] | : | Ñaït yeâu caàu/ Pass
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
| - Thöû löïc keùo ñaàu truï | [7 empty] | : | Ñaït yeâu caàu/ Pass
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
2000
F
L=12000
250