## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0630-03
Ngaøy/Date: |  | 30/6/2021. |  |  | Ban haønh laàn 1, soá baûn 03 / The 1st isuse, 03 copies | [9 empty] | Trang 1/3
1 | Ñôn vò yeâu caàu/Custommer |  |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM THUÛ ÑÖÙC 1(TDC1 JSC).
2 | Ñòa chæ / Address |  |  |  |  | : | SOÁ 234-ÑT 747-AÁP THANH LÖÔNG-X THAÏNH PHÖÔÙC-H.TAÂN UYEÂN-T. BÌNH DÖÔNG.
3 | Chuû Ñaàu tö/Proj.Investor |  |  |  |  | : | COÂNG TY ÑIEÄN LÖÏC BÌNH PHÖÔÙC.
4 | Nhaø thaàu/Contractor |  |  |  |  | : | COÂNG TY TNHH TM TV XD CAÀU ÑÖÔØNG PHÖÔÙC TIEÁN.
5 | Coâng trình/ Project |  |  |  |  | : | SÖÛA CHÖÕA LÔÙN LÖÔÙI ÑIEÄN KHU VÖÏC TP ÑOÀNG XOAØI NAÊM 2021.
6 | Teân maãu/Sample name |  |  |  |  | : | TRUÏ ÑIEÄN BTLT ÖÙNG LÖÏC TRÖÔÙC- Loaïi : PC.I-12-190-5.4kN-N2.
7 | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 truï / pole
8 | Ngaøy thöû/Testing date |  |  |  |  | : | 28/6/2021.
9 | Kyù hieäu maãu/ |  |  |  |  | : | TDC1-PCI-12-190-5.4kN-N2-SX: 06/2021.
Code of sample
10 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847: 2016; TCVN 9334 : 2012.
Test method
11 | Ñieàu kieän thöû nghieäm
Maãu ñöôïc thöû nghieäm taïi nhaø maùy : soá 234- ÑT 747,AÁp Taân Löông,Xaõ Thaïnh Phöôùc,Huyeän Taân Uyeân- Tænh Bình Döông , coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan. The sample was tested at Factory - of TDC1 Company, with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá : | [6 empty] | 40 | MPa
Concrete with design grade :
| - Thöû keùo ñaàu truï danh ñònh Pn : kN | [7 empty] | 5.4 | 550.8 | kGf
Nominal load test at the top of pole :
| - Thöû keùo ñaàu truï Phaù huûy N 2 : Pu = | [7 empty] | 10.8 | 1101.6 | kGf
Breaking Load test at the top of pole : Pu max
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: 12-540-N=2-TDC1/01 ,thaùng 02/2020 cuûa COÂNG TY COÅ PHAÀN BTLT THUÛ ÑÖÙC 1 (TDC1). Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing No: 12-540-N=2-TDC1/01; 02/2020 of THUDUC 1 JSC(TDC1).
Ngöôøi thöïc hieän | [6 empty] | Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyeãn Vaên Hoàng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0630-03
Ngaøy/Date: |  | 30/6/2021. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
12 | Thieát bò thöû nghieäm chính:
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
- Löïc keá coù thang ño 2000 kgf, vaïch chia 01 kgf.
- Boä caên laù töø 0.02 ñeán 1.00 mm.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
13 | Keát quaû Thöû nghieäm/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû TN Test result |  |  | Ñaùnh giaù Comments
1 | TDC1-PCI-12-190-5.4kN-N2-SX: 06/2021. |  |  | 1 | Chieàu daøy lôùp beâ toâng vaø vöõa | [5 empty] | mm
|  |  |  | * | Chieàu daøy lôùp beâ toâng taïi thaân coät | [5 empty] | mm | ≥ 15 |  | 24 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøy lôùp vöõa traùt taïi ñænh | [6 empty] | ≥ 25 |  | 25 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøy lôùp vöõa traùt taïi ñaùy | [6 empty] | ≥ 35 |  | 35 |  |  | Ñaït/ Pass
|  |  |  | 2 | Ñoä nhaün beà maët | [5 empty] | mm
|  |  |  | * | Nhaün ñeàu | [6 empty] | Nhaün ñeàu |  | Nhaün ñeàu |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu saâu loã roã ôû meùp khuoân | [5 empty] | mm | ≤ 2 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøi loã roã ôû meùp khuoân | [6 empty] | ≤ 15 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | 3 | Kích thöôùc loã roã treân maët coät | [5 empty] | mm
|  |  |  | * | Maët ngoaøi | [6 empty] | D ≤ 10 ; L ≤ 5 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | * | Maët muùt coät | [6 empty] | D ≤ 8 ; L ≤ 3 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | * | Veát loài loõm treân thaân coät | [6 empty] | ≤ 2 ; ≤ 2 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | 4 | Nöùt beà maët | [5 empty] | mm
|  |  |  | * | Veát nöùt voøng quanh coät | [6 empty] | 0 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | * | Beà roäng Veát nöùt | [6 empty] | 0.05 ≤ |  | 0 |  |  | Ñaït/ Pass
|  |  |  | 5. Kích thöôùc cô baûn | [6 empty] | mm
|  |  |  | - | Chieàu daøi | [6 empty] | 12000(+25,-10) |  | 12005 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 190 (+4,-2) |  | 190
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 50 (+7;-5) |  | 55
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 350 (+4,-2) |  | 351
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 60 (+7;-5) |  | 66
|  |  |  | 6.Cöôøng ñoä beâ toâng (baèng buùa thöû) | [6 empty] | MPa | min 50 |  | 59 |  |  | Ñaït/ Pass
|  |  |  | 7. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,25 |  | 0 |  |  | Ñaït/ Pass
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0630-03
Ngaøy/Date: |  | 30/6/2021. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
13.1. | Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây:
SÔ ÑOÀ THÖÛ KEÙO LÖÏC ÑAÀU TRUÏ
13.2. | Keát quaû Thöû nghieäm Löïc keùo ñaàu truï/ Test result of Load
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | TDC1-PCI-12-190-5.4kN-N2-SX: 06/2021. |  |  | 4. Löïc keùo ñaàu truï/ Tensile load at the top pole | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
[12 empty] | 1.35 | 2.7 | 4.05 |  | 5.4 | Deload
[12 empty] | 137.7 | 275.4 | 413.1 |  | 550.8
|  |  |  | - | Ñoä dòch chuyeån/ Deformation | [5 empty] | mm
|  |  |  | ÔÛ vò trí 1/ at position 1 | [7 empty] | 33 | 76 | 137 |  | 232 | 16
|  |  |  | - | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks
|  |  |  | .- | Soá löôïng veát nöùt noái tieáp voøng quanh thaân truï | [5 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks, continuous on the pole.
|  |  |  | - | Beà roäng cuûa veát nöùt lôùn nhaát, | [5 empty] | mm | 0 | 0 | 0 |  | 0 | 0
Width of the maximum cracks
|  |  |  | - | Löïc keùo tôùi haïn Pu; N=2.0 | [5 empty] | KN (kGf) | TRUÏ CHÖA PHAÙ HUÛY KHI Pu=N2= 10.8 KN (1102 KGF)
Breaking Load Pmax
14 | Nhaän xeùt/ Comments |  |  |  |  | :
Caên cöù tieâu chuaån 5847 : 2016 vaø baûn veõ thieát keá truï ñieän 12-F540-N=2-TDC1/02; 02/2020 cuûa COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM THUÛ ÑÖÙC 1.Keát quaû thöû nghieäm cho thaáy :
Based on TCVN 5847: 2016 and designed drawing for PCRC Electricad pole type 12-F540-N=2.0-TDC1/02; 02/2020 result of THUDUC1 JSC ,the above test result of the tested pole show that:
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
Dimension
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
Grade of concrete
| - Thöû löïc keùo ñaàu truï | [7 empty] | : | Ñaït yeâu caàu/ Pass
Tensile load at the top of pole test
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
2000
F
L=12000
250