## CAU KIEN BT
1 | 2 |  | 3 | 4 | [5 empty] | 5 | 6 |  | 7 | 8 | 9 | 10
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [12 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [12 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [12 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [12 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [6 empty] | LAS-XD 506
0630-04
Ngaøy/Date: |  | 30/6/2021. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse, 3 copies | [6 empty] | Trang 1/1
1 | Ñôn vò yeâu caàu/Custommer |  |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM THUÛ ÑÖÙC 1(TDC1 JSC).
2 | Ñòa chæ / Address |  |  |  |  | : | SOÁ 234-ÑT 747-AÁP THANH LÖÔNG-X THAÏNH PHÖÔÙC-H.TAÂN UYEÂN-T. BÌNH DÖÔNG.
3 | Chuû Ñaàu tö/Proj.Investor |  |  |  |  | : | COÂNG TY ÑIEÄN LÖÏC BÌNH PHÖÔÙC.
4 | Nhaø thaàu/Contractor |  |  |  |  | : | COÂNG TY TNHH TM TV XD CAÀU ÑÖÔØNG PHÖÔÙC TIEÁN.
5 | Coâng trình/ Project |  |  |  |  | : | SÖÛA CHÖÕA LÔÙN LÖÔÙI ÑIEÄN KHU VÖÏC TP ÑOÀNG XOAØI NAÊM 2021.
6 | Teân maãu/Sample name |  |  |  |  | : | ÑAØ CAÛN 1200X200/ POLE FOUNDATION 1200X200.
7 | Kyù hieäu maãu |  |  |  |  | : | ÑC 1200X200 : SX 02/2021.
8 | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 Caùi
9 | Ngaøy thöû/Testing date |  |  |  |  | : | 28/6/2021.
10 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 9334:2012;TCXDVN 239:2006.
Test method
11 | Ñieàu kieän thöû nghieäm / Test condition:
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
Concrete test Hammer, measuring range (10-70) Mpa, type N
- Ñaø caûn ñöôïc saûn xuaát theo baûn veõ cuûa COÂNG TY COÅ PHAÀN BTLT THUÛ ÑÖÙC 1 (TDC1) .
Pole foundation were produced base on the designed drawing of THU DUC 1 CENTRIFUGED CONCRETE JOINT STOCK COMPANY (TDC1)
- Treân moãi caáu kieän ñöôïc thöû nghieäm taïi 3 vuøng khaùc nhau.Treân moãi vuøng thöû nghieäm coù dieän tích khoaûng (200x300) mm,ñöôïc maøi nhaün,thöû 10 ñieåm baèng buùa thöû.
On the each testing element was tesedt in 3 positions.In each test position about (200X300)mm,wich was ground smooth,took 10 rebound readings.
12 | Keát quaû/ Test result |  |  |  |  | :
| Teân caáu kieän |  |  | Tình traïng beà maët beâ toâng |  |  |  | Cöôøng ñoä neùn öôùc tính.Mpa ( baèng buùa thöû) |  | Kích thöôùc/Dimension, mm
| Name of element |  |  | Concrete surface status |  |  |  | Estimated Compressive strength , MPa |  | Daøi / Length |  |  | Roäng/ Broard |  | Cao / High
| ÑC 1200X200 : SX 02/2021. |  |  | Khoâ, Khoâng nöùt, Khoâng roã. |  |  |  | 29(min 20) |  | 1205 |  |  | 203 |  | 201/64
Nhaän xeùt keát quaû Thöû Nghieäm:KÍCH THÖÔÙC; MAÙC BEÂ TOÂNG Phuø hôïp vaø Ñaït yeâu caàu Thieát Keá.
Ngöôøi thöïc hieän | [6 empty] | Phoøng TN |  | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory |  | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyễn Văn Hồng Chi |  | Nguyeãn Thò Thuûy
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [8 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only | [8 empty] | 07.07WP09.R0-From07.07-REP38.R0