## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [14 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [14 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [14 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [14 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0228-01
Ngaøy/Date: |  | 28/02/2022. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 1/3
1 | Ñôn vò yeâu caàu/Custommer |  |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM THUÛ ÑÖÙC LONG AN.
2 | Ñòa chæ / Address |  |  |  |  | : | AÁP 3-XAÕ AN THAÏNH -H.BEÁN LÖÙC-T. LONG AN.
4 | Chuû Ñaàu Tö/Proj.Investor |  |  |  |  | : | COÂNG TY ÑIEÄN LÖÏC BÌNH PHUÙ.
5 | Nhaø Thaàu/Contractor |  |  |  |  | : | COÂNG TY TNHH KD XAÂY DÖÏNG ÑIEÄN BAÛO NGUYEÂN.
6 | Coâng trình/ Project |  |  |  |  | : | SÖÛA CHÖÕA LÔÙN TSCÑ LÖÔÙI TRAÏM HAÏ THEÁ KHU VÖÏC PHÖÔØNG BÌNH TRÒ ÑOÂNG,BÌNH TRÒ ÑOÂNG A,BÌNH HÖNG HOØA B QUAÄN BÌNH TAÂN NAÊM 2022.
7 | Teân Maãu/Sample name |  |  |  |  | : | TRUÏ ÑIEÄN BTLT DÖÏ ÖÙNG LÖÏC-Loaïi PC.I-8.5m-160-3.0 (306kGf)-K2.
8 | Soá löôïng maãu/ Quantity |  |  |  |  | : | 01 truï / pole
9 | Ngaøy thöû/Testing date |  |  |  |  | : | 28/02/2022.
10 | Kyù hieäu maãu/Sample Code |  |  |  |  | : | TDCLA-PC.I-8.5-160-300-K=2; SOÁ 339 -T 12/2021.
11 | Tieâu chuaån thöû nghieäm |  |  |  |  | : | Tham khaûo/ Refer to TCVN 5847: 2016; TCVN 9334 : 2012.
Test method
12 | Ñieàu kieän thöû nghieäm :
Maãu ñöôïc thöû nghieäm taïi nhaø maùy :AÁp 3,Xaõ An Thaïnh,Huyeän Beán Löùc- Tænh Long An, coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan. The sample was tested at Factory - of TDC Long An Company, with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá : | [6 empty] | 40 | MPa
Concrete with design grade :
| '- Thöû keùo ñaàu truï danh ñònh Pn : | [7 empty] | KN | 3 | 306 | kGf
Nominal load test at the top of pole :
| '- Thöû keùo ñaàu truï Phaù Huûy: Pu : | [7 empty] | KN | 6 | 612 | kGf
Breaking Load test at the top of pole : Pu max
- Truï ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: 8.5-300-TDCLA/02 ,thaùng 06/2018 cuûa COÂNG TY COÅ PHAÀN BTLT THUÛ ÑÖÙC LONG AN (TDCLA JSC). Prestressed Centrifugal Reinforced Concrete Electrical Pole were produced base on the designed drawing No: 8.5-300-TDCLA/02; 06/2018 of TDCLA JSC.
Ngöôøi thöïc hieän | [6 empty] | Tröôûng Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [6 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [6 empty] | Nguyeãn Vaên Hoàng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc keát KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0228-01
Ngaøy/Date: |  | 28/02/2022. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
13 | Thieát bò thöû nghieäm chính:
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm
- Buùa thöû beâ toâng, thang ño (10 – 70) MPa, loaïi N;
- Löïc keá coù thang ño 2000 kgf, vaïch chia 01 kgf.
- Boä caên laù töø 0.02 ñeán 1.00 mm.
- Kính phoùng ñaïi 4 mm, vaïch chia 0,05 mm.
14 | Keát quaû thöû nghieäm Ngoaïi quan & Kích thöôùc/ Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  |  | Ñaùnh giaù Comments
1 | TDCLA-PC.I-8.5-160-300-K=2; SOÁ 339 -T 12/2021. |  |  | 1 | Chieàu daøy lôùp beâ toâng vaø vöõa | [5 empty] | mm
|  |  |  | * | Chieàu daøy lôùp beâ toâng taïi thaân coät | [5 empty] | mm | ≥ 15 |  | 21 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøy lôùp vöõa traùt taïi ñænh | [6 empty] | ≥ 25 |  | 25 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøy lôùp vöõa traùt taïi ñaùy | [6 empty] | ≥ 35 |  | 35 |  |  | Ñaït/ Pass
|  |  |  | 2 | Ñoä nhaün beà maët | [5 empty] | mm
|  |  |  | * | Nhaün ñeàu | [6 empty] | Nhaün ñeàu |  | Nhaün ñeàu |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu daøi loã roã ôû meùp khuoân | [5 empty] | mm | ≤ 15 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | * | Chieàu saâu loã roã ôû meùp khuoân | [6 empty] | ≤ 2 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | 3 | Kích thöôùc loã roã treân maët coät | [5 empty] | mm
|  |  |  | * | Maët ngoaøi | [6 empty] | D ≤ 10 ; L ≤ 5 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | * | Maët muùt coät | [6 empty] | D ≤ 8 ; L ≤ 3 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | * | Veát loài loõm treân thaân coät | [6 empty] | D ≤ 2 ; L ≤ 2 |  | 0 ; 0 |  |  | Ñaït/ Pass
|  |  |  | 4 | Nöùt beà maët | [5 empty] | mm
|  |  |  | * | Veát nöùt voøng quanh coät | [6 empty] | 0 |  | 0 |  |  | Ñaït/ Pass
|  |  |  | * | Beà roäng Veát nöùt | [6 empty] | 0.05 ≤ |  | 0 |  |  | Ñaït/ Pass
|  |  |  | 5. Kích thöôùc cô baûn | [6 empty] | mm
|  |  |  | - | Chieàu daøi | [6 empty] | 8500(+25,-10) |  | 8500 |  |  | Ñaït/ Pass
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñænh | [6 empty] | 160 (+4,-2) |  | 160
|  |  |  | - | Chieàu daøy ñænh | [6 empty] | 50 (+7;-5) |  | 50
|  |  |  | - | Ñöôøng kính ngoaøi taïi ñaùy | [6 empty] | 255 (+4,-2) |  | 256
|  |  |  | - | Chieàu daøy ñaùy | [6 empty] | 60 (+7;-5) |  | 65
|  |  |  | 6.Cöôøng ñoä beâ toâng (baèng buùa thöû). | [6 empty] | MPa | 40 |  | 59 |  |  | Ñaït/ Pass
|  |  |  | 7. Beà roäng veát nöùt lôùn nhaát taïi Pn | [6 empty] | mm | max 0,25 |  | 0.05 |  |  | Ñaït/ Pass
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
Số/ Ref.No: |  |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0228-01
Ngaøy/Date: |  | 28/02/2022. |  |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây:
1400
SÔ ÑOÀ THÖÛ KEÙO LÖÏC ÑAÀU TRUÏ
14.1. | Keát quaû thöû nghieäm Löïc gaây nöùt & Phaù huûy /Test result
TT | Kyù hieäu maãu/ Code of sample |  |  | Chæ tieâu kieåm tra/ Characteristics | [6 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
2 | TDCLA-PC.I-8.5-160-300-K=2; SOÁ 339 -T 12/2021. |  |  | 8. Löïc keùo ñaàu truï / Tensile load at the top pole | [6 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
[12 empty] | 0.75 | 1.5 | 2.25 |  | 3 | Deload
[11 empty] | kGf | 76.5 | 153 | 229.5 |  | 306
|  |  |  | 1 | Ñoä dòch chuyeån | [5 empty] | mm
|  |  |  | * | Ñoä dòch chuyeån ôû vò trí 1 | [6 empty] | 19 | 41 | 69 |  | 125 | 13
|  |  |  | * | Soá löôïng veát nöùt, | [5 empty] | veát | 0 | 0 | 0 |  | 5 | 0
|  |  |  | * | Beà roäng cuûa veát nöùt lôùn nhaát, (max 0.25mm). | [5 empty] | mm | 0 | 0 | 0 |  | 0.05 | 0
|  |  |  | 2 | Löïc keùo tôùi haïn Pu (K=2) | [5 empty] | kN (kGf) | Pu=K2= 607 kGf,TRUÏ ÑIEÄN CHÖA PHAÙ HUÛY.
15 | Nhaän xeùt/ Comments |  |  |  |  | :
Caên cöù tieâu chuaån 5847:2016 vaø baûn veõ thieát keá truï ñieän 8.5-300 kGf-K2, Thaùng 6/2018 ; cuûa COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM THUÛ ÑÖÙC LONG AN (TDCLA JSC) Thieát keá.Keát quaû thöû nghieäm cho thaáy:
Based on TCVN 5847:2016 and designed drawing for PCRC Electricad pole type 8.5-300 kGf -K2; 06/2018 result of TDCLA JSC designed ,the above test result of the tested pole show that:
| - Ngoaïi quan | [7 empty] | : | Ñaït yeâu caàu/ Pass
| - Kích thöôùc | [7 empty] | : | Ñaït yeâu caàu/ Pass
| - Maùc beâ toâng | [7 empty] | : | Ñaït yeâu caàu/ Pass
| - Thöû löïc keùo ñaàu truï | [7 empty] | : | Ñaït yeâu caàu/ Pass
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [17 empty] | 07.07WP09.R0-From07.07-REP38.R0
F
250
L=8500