## COT TRON
COÂNG TY COÅ PHAÀN TÖ VAÁN KIEÅM ÑÒNH XAÂY DÖÏNG PHÍA NAM
SOUTH CONSTRUCTION INSPECTION CONSULTANT JOINT STOCK COMPANY
|  |  | Truï sôû & PTN : phoøng B01-Toøa nhaø eTUNNEL | [13 empty] | Vaên phoøng ñaïi dieän: Phoøng G01- Toøa nhaø PLUG-IN
|  |  | L11-L12 Mieáu Noåi P.3 Bình Thaïnh HCM, Vieät Nam | [13 empty] | 223 Ñieän Bieân Phuû P.15 Bình Thaïnh HCM, Vieät Nam
|  |  | ÑT : (84).8.5 170886 – Fax: (84).8. 5170335 | [13 empty] | ÑT : (84).8. 8404415 – Fax: (84).8. 8404412
|  |  | E-mail: scic@dmc.vn | [13 empty] | website: http://www.dangminh.vn
Số/ Ref.No: |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0422-01
Ngaøy/Date: |  | 22/04/2022 |  | Ban haønh laàn 1, soá baûn 03 / The 1st isuse, 03 copies | [9 empty] | Trang 1/3
1. | Teân Maãu/ Sample name |  |  |  | : | COÄT ÑIEÄN BTLT TIEÀN AÙP-LOAÏI 16-PC-10.0, k = 2,0
| Kyù hieäu maãu/ |  |  |  | : | 16-PC-10.0, Số 01-03/2022 (ÑKÑ 230, Ngoïn 10 m, Goác 06 m)
Code of sample
2. | Coâng trình/ Project |  |  |  | :
3. | Soá löôïng maãu/ Quantity |  |  |  | : | 01 truï / pole
4. | Ngaøy thöû/ Testing date |  |  |  | : | 20/04/2022
5. | Ñôn vò yeâu caàu/Custommer |  |  |  | : | COÂNG TY COÅ PHAÀN BEÂ TOÂNG LY TAÂM AN GIANG
| Ñòa chæ/ Address |  |  |  | : | Quoác loä 91, phöôøng Myõ Thôùi, TP.Long Xuyeân, tænh An Giang
6. | Tieâu chuaån thöû nghieäm |  |  |  | : | TCVN 5847:2016; Tham khaûo/ Refer to TCVN 9334:2012.
Test method
7. | Ñieàu kieän thöû nghieäm/ Test condition:
- Maãu ñöôïc thöû nghieäm taïi Coâng ty Coå phaàn Beâ toâng Ly taâm An Giang,
coù söï chöùng kieán cuûa khaùch haøng vaø caùc beân lieân quan.
The sample was tested at An Giang Centrifuged Concrete Joint Stock Company,
with the witness of the customer and related parties.
- Soá löôïng vaø loaïi maãu thöû theo chæ ñònh cuûa khaùch haøng vaø caùc beân lieân quan.
Quantity and type of sample were determined by the client and related parties.
| - Beâ toâng maùc thieát keá: | [5 empty] | 40 | MPa
Concrete with design grade:
| - Taûi troïng thieát keá truï ñieän PC: | [5 empty] | 10 | kN
Design load of PC Electrical Pole:
- Coät ñieän ñöôïc saûn xuaát theo baûn veõ thieát keá soá: 01/16-PC-10.0/ACECO/02-22 cuûa Coâng ty
Coå phaàn Beâ toâng Ly taâm An Giang
Electrical pole was produced based on the designed drawing No. 01/16-PC-10.0/ACECO/02-22
of An Giang Centrifuged Concrete Joint Stock Company
Ngöôøi thöïc hieän | [5 empty] | Phoøng TN | [5 empty] | P.Giaùm Ñoác
Tested by | [5 empty] | Chief of Laboratory | [5 empty] | Vice Director
Nguyeãn Huy Tieán | [5 empty] | Nguyeãn Vaên Hoàng Chi | [5 empty] | Nguyeãn Thò Thuûy
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [16 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0422-01
Ngaøy/Date: |  | 22/04/2022 |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 2/3
8. | Thieát bò thöû nghieäm chính/Main equipment for testing:
- Thöôùc theùp daøi 20 m, vaïch chia 1 mm/ Tape rule 20 m, measuring range 1 mm
- Thöôùc caëp, vaïch chia 0,02 mm/ Vernier caliper, division 0,02 mm
- Boä caên laù 0.02 ñeán 1.00 mm/ Feeler gauge range 0.02 to 1.00 mm
- Kính ño veát nöùt/ Microscope 4 mm/ 0,02 mm
- Buùa thöû beâ toâng/ Concrete test hammer (10 – 70) MPa, type N
- Caân treo ñieän töû/ Electronic crane scales 3000 kgf/ 1 kgf
Truï ñieän ñöôïc thöû keùo theo sô ñoà döôùi ñaây/ The test was carried out as the sketch below:
Sketch for tensile load test at the the top of pole
9. | Keát quaû thöû nghieäm/ Test result
TT | Chæ tieâu kieåm tra/ Characteristics | [8 empty] | Ñôn vò/ Unit | Yeâu caàu Requirement |  | Keát quaû thöû nghieäm Test result |  |  | Ñaùnh giaù Comments
9.1. | Ngoại quan/ Appearance | [14 empty] | Ñaït/ Pass
- Độ nhẵn bề mặt (mặt ngoài)/ Surface smoothness
| + Kích thöôùc loã roã/ Dimension of skin hole | [8 empty] | mm
| Ñöôøng kính/ Diameter | [9 empty] | Max 10 |  | 0
| Chieàu saâu/ Depth | [9 empty] | Max 5 |  | 0
| + Veát loài loõm/ Cambers | [9 empty] | Max 2 |  | 1
- Nöùt beà maët/ Surface cracking
| + Bề rộng/ Width | [8 empty] | mm | Max 0,05 |  | 0
| + Vết nứt nối tiếp vòng quanh thaân cột | [8 empty] | veát | 0 |  | 0
| Cracks continue around the pole | [8 empty] | Cracks
9.2. | Kích thöôùc cô baûn/ Dimension | [8 empty] | mm | [5 empty] | Ñaït/ Pass
| - Chieàu daøi/ Length | [9 empty] | 16000 (+50;-10) |  | 16010
| - Ñöôøng kính ngoaøi taïi ñænh/ Outside diameter at top | [9 empty] | 230 (+4;-2) |  | 232
| - Chieàu daøy ñænh/ Wall-thickness at top | [9 empty] | 70 (+7;-5) |  | 73
| - Ñöôøng kính ngoaøi taïi ñaùy/ Outside diameter at bottom | [9 empty] | 443 (+4;-2) |  | 445
| - Chieàu daøy ñaùy/ Wall-thickness at bottom | [9 empty] | 90 (+7;-5) |  | 94
9.3. | Cöôøng ñoä neùn beâ toâng (Baèng buùa thöû beâ toâng) | [8 empty] | MPa | min | 40 | 64 |  |  | Ñaït/ Pass
Compressive strength of concrete (concrete Hammer Test)
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [16 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
Số/ Ref.No: |  |  |  | PHIEÁU KEÁT QUAÛ THÖÛ NGHIEÄM TEST REPORT | [9 empty] | LAS-XD 506
0422-01
Ngaøy/Date: |  | 22/04/2022 |  | Ban haønh laàn 1, soá baûn 03/ The 1st isuse,03 copies | [9 empty] | Trang 3/3
TT | Chæ tieâu kieåm tra/ Characteristics | [8 empty] | Ñôn vò/ Unit | Keát quaû thöû nghieäm Test result
9.4. | Khaû naêng chòu taûi/ Lateral load capacity | [9 empty] | Möùc taêng taûi/ Rate of applying load
| ° Löïc keùo ñaàu truï | [8 empty] | % kN | 25% | 50% | 75% |  | 100% | Xaû taûi
| Tensile load at the top pole | [9 empty] | 2.5 | 5 | 7.5 |  | 10 | Deload
[10 empty] | (kgf) | 254.842 | 509.684 | 764.526 |  | 1019.368
| - Ñoä dòch chuyeån/ Deformation | [8 empty] | mm
| ÔÛ vò trí 1/ at position 1 | [9 empty] | 50 | 124 | 202 |  | 346 | 19
| - Soá löôïng veát nöùt/ Quantity of the visual cracks | [8 empty] | veát | 0 | 0 | 0 |  | 8 | 0
| - Soá löôïng veát nöùt noái tieáp voøng quanh thaân coät | [8 empty] | veát | 0 | 0 | 0 |  | 0 | 0
Quantity of the visual cracks,continuous on the pole
| - Beà roäng cuûa veát nöùt lôùn nhaát | [8 empty] | mm | 0 | 0 | 0 |  | 0.06 | 0
Width of the maximum cracks
(Theo yeâu caàu TCVN 5847-2016, max 0,25 mm)
| ° Löïc keùo tôùi haïn Pu: | [8 empty] | kN (kgf) | Pmax = 20,55 (2095 kgf)
Breaking Load Pmax
10. | Nhaän xeùt/ Comments:
Caên cöù tieâu chuaån TCVN 5847 : 2016 vaø baûn veõ thieát keá coätï ñieän 16 m cuûa Coâng ty Coå phaàn
Beâ toâng Ly taâm An Giang. Keát quaû thöû nghieäm cho thaáy:
Based on TCVN 5847: 2016 and designed drawing for Electricad pole type 16 m of An Giang
Centrifuged Concrete Joint Stock Company, the above test result of the tested pole show that:
| - Ngoại quan/ Appearance | [7 empty] | : Ñaït yeâu caàu/ Pass
| - Kích thöôùc/ Dimension | [7 empty] | : Ñaït yeâu caàu/ Pass
| - Maùc beâ toâng/ Grade of concrete | [7 empty] | : Ñaït yeâu caàu/ Pass
| - Thöû löïc keùo ñaàu truï | [7 empty] | : Ñaït yeâu caàu/ Pass
Tensile load at the top of pole test
1. Caùc KQTN ghi trong phieáu naøy chæ coù giaù trò ñoái vôùi maãu do khaùch haøng chæ ñònh | [16 empty] | 07.07WP09.R0-From07.07-REP38.R0
Test result are valid for the namely submitted samples only
L = 16.000
2500
250
1
Ngaøm/ Fixed connection
Coät/ Pole
F
Maët bích lieân keát baèng bu loâng